Plainfield Community Church

1094 Route 12A

675-6510

Permit # 2010-38

Map/ID # 107/6

Renovation of basement

04-14-10	Permit Applying, Plainfield Community Church, Route 12A. I met with the Pastor, contractor and board member to go over the work they are planning to do. In the basement two short walls were removed and they want to make the bathroom HC accessible; provide additional support to the log beams; insulate the stone foundation; upgrade the kitchen; install smoke detectors and exit and emergency lights; change stairs to accommodate HC by installing an electric chair system; and to install a fire code drop ceiling. Upstairs they want to move the existing hall to the front to accommodate the new stairs; install exit and emergency lighting; install smoke detectors; replace outside doors with emergency push bars; add some receptacles along the two outside walls; and to fix the two doors from the sanctuary to close without latching. I made several suggestions and comments as well as answering their questions. They will be applying for a permit.

Time 1.1

09-14-10	Permit 2010-38, 1094 Route 12A. I inspected all the new joists, location for the new stairs, and the forms and rebar for the short concrete wall that will be against the stone foundation. Upstairs they rebuilt the platform with two layers of ¾ plywood and new supporting members. They removed all the old log joists and the new boards are 12 inches on center. Looks good, they will call when the rough in electrical is ready.

Time 0.9

11-11-10	Permit 2010-38, 1094 Route 12A. I inspected the new meter panel and conduit for the new aerial service and the 200 ampere panel in the basement. I also inspected the rough in wiring as well as the new propane forced hot air furnaces. I suggested they put screens over the PVC vent pipes to keep out unwanted guests.

Time 0.4

12-16-10	Permit 2010-38, 1094 Route 12A. I went by and inspected the upgraded electrical service entrance (200 ampere) so I could notify PSNH it was okay to move service to new panel.

Time 0.2

02-05-11	Permit 2010-38, 1094 Route 12A. I was called to inspect more of the electrical wiring so they could start installing some sheetrock and to inspect more of the work that was completed. We discussed the clearance needed between the bottom of the rear stairs and the inside door. Since the door swings out I told them you need enough room to be off the steps to open the three foot door towards you. It looks like they will have two feet if the door frame is constructed at the inside edge of the foundation.

Time 0.7

04-02-11	Permit 2010-38, 1094 Route 12A. I inspected the new exit door at the rear of the church with the installed panic bar and electrical wiring on both floors as well as the organ loft. Emergency/Exit lights were installed above the two sanctuary exits and the other locations were ready to be installed when the walls are painted. We discussed the locations and number of smoke detectors for the basement. The plan is for five detectors

with the location near the kitchen area will be a heat detector as well as the one in the kitchen. I let them know that the detector instructions will let them know how many square feet of area they support and they need to go by that. I suggested that they install a smoke/heat detector above the drop ceiling in the basement. They had the correct amount of GFI receptacles installed in the kitchen and more that the requited two circuits. Looked okay.

Time 0.7

05-09-11	Permit 2010-38, 1094 Route 12A. I received a call to inspect the plumbing in the kitchen and bathroom in the basement. Looked okay and told them they could continue to close in the walls with sheetrock.

Time 0.4

David H Lersch

Plainfield Building Inspector