Mac’s Happy Acres

259 River Road

298-8838

Permit # 2012-14

Map/Lot 108/2

Renovation of entire house

1121 Route 12A

03-18-12	Permit 2012-14, 1121 Route 12A. Telephone call when I was on vacation.  John Mayette house, needed rough in for part of renovation-no permit yet.

I told them I would stop by when I got back and to take a few pictures as the work was only a little of what is going to be done.

Time 0.1

07-10-12	Permit 2012-14, 1121 Route 12A. I stopped by as the house was moved over and Scott was excavating for the foundation. I asked what there time schedule was for the footer and walls and how long they had to wait to put the house on the foundation. They were hoping to do the footer Wednesday and they would call.

0.2

07-12-12	Permit 2012-14, 1121 Route 12A. I stopped by and they were just assembling the footer forms and they said they should be ready around noon to pour.

Time 0.2

07-12-12	Permit 2012-14, 1121 Route 12A. I stopped by and they were almost ready to call for concrete. All the rebar was in and was being suspended by wires. Ground wire was installed as I requested, clamped to rebar. I gave the okay to pour.

Time 0.2

07-30-12	Permit 2012-14, 1121 Route 12A. I stopped to inspect the basement prior to them pouring the basement floor. The drains in place, gravel and wire mesh, okay to pour.

Time 0.2

08-22-12	Permit 2012-14, 1121 Route 12A. I stopped by as they were working upstairs and I never looked at some of the wiring that was done when I was out of town. The house is on its new foundation and all the chimneys are properly supported in the basement. They had sprayed foam insulation on part of the front of the house. I noticed the metal electrical boxes were two small for the 12-2 wires that were installed and one had three 12-2 wires in it. The box size wouldn’t support one 12-2 with a switch or receptacle. The wires were cut two short (need six inches of wire sticking out of the box). I suggested using plastic boxes of the right capacity. A new electrical panel is going in and I let him know that it would fall under the current code, requiring arc fault breakers. since they will be replacing windows upstairs, the bedrooms will need one egress window per bedroom. The wires should be longer at the box, but with the foam insulation it will be very difficult to pull new wires. After I got home I got out the code book, copied the page with the box capacities on it and added some notes as well.

Time 0.6

08-30-12	Permit 2012-14, 1121 Route 12A. I stopped by to inspect the electrical boxes to see if they were replaced as I noticed there was scrap sheetrock in the yard. Most of the boxes were changed and additional length of wire was in the boxes. They were installing sheetrock upstairs and those boxes were replaced and were okay. There is still some boxes to be replaced, but those areas won’t have sheetrock installed yet. While I was there Mac called to have me inspect the boxes, etc. and I told him I was there and it was okay.

Time 0.5

09-06-12	Permit 2012-14, 1121 Route 12A. I dropped off the oil burning permit so it could be filled out for the Fire Chief. The oil boiler was removed and set in the basement after the house was moved on the new foundation, so it will have to be reinstalled.

Time 0.2

09-25-12	Permit 2012-14, 1121 Route 12A. PSNH was connecting power to the meter panel on the house. I went by after the were completed and inspected the service entrance to the meter panel and also the electrical cable from the meter panel to the 200 ampere circuit panel. Everything looked okay.

Time 0.4

10-02-12	Permit 2012-14, 1121 Route 12A. Someone was working on doubling up the joists for the second floor as they want to use the second floor above the kitchen for a bedroom, previously was only attic space. Looked over the plans for the kitchen and discussed the electrical circuits and the placement of receptacles.

Time 0.7

10-10-12	Permit 2012-14, 1121 Route 12A. Tom called to have me inspect the kitchen rough in electrical wiring. Looked okay except one receptacle had the wire around the screw CCW instead of CW. I let Tom know, he will fix it.

Time 0.2

10-23-12	Permit 2012-14, 1121 Route 12A. Tom called to have me inspect the rough in plumbing by Doug Freeland. Looked okay.

Time 0.5

02-14-13	I went and did a final CO inspection at John Meyette's old residence on Rte.12-A with Tom McNamara on 2/7/13. Everything looked okay. I did tell him to block off the front porch where there are no steps at this time. They are going to bring the final grade up in the spring before putting the final steps in place. Other than that all systems are working and Frank Currier (Fire Chief) had inspected the furnace.

I'd say the two projects are ready for CO's.

Time 0.5 - 2 miles

Win Spencer Jr.

02-17-13	Issued CO and emailed to Town Hall

Time 0.3

David H Lersch

Plainfield Building Inspector