Dave & Marketta Steck

184 Willow Brook Road

352-496-2956 (David 469-3177)

Permit #2008-58

Permit #2010-44

Permit # 2011-44

Map/Lot 225/11

08-27-08	Permit 2008-58, 184 Willow Brook Road. Inspected the footer forms for the new house. No one was there and the ground wire wasn’t installed yet, waited about fifteen minutes, left, saw contractor truck on my way to the town hall, turned around and went back. Contractor was installing ground wire in the footer and all looked okay except I asked them to connect the rebar in the upper level to the rebar in the lower section. They agreed and I told them they could pour.

Time 1.0

08-28-08	Permit 2008-58, 184 Willow Brook Road. Inspected wall forms, okay. Told them they could pour.

Time 0.6

09-05-08	Permit 2008-58 184 Willow Brook Road. Inspected perimeter drains. Looked okay, let them know they could backfill.

Time 0.3

08-28-09	Permit 2008-58, 184 Willow Brook Road. Inspected the panels and wiring for the temporary electrical service. There were several open positions in the circuit panel and were duct taped and need to have plastic covers installed, notified Dave. Also cable from head to meter panel just coiled and not clamped to the tree where the temporary power will be. I am waiting for Dave to let me know when items are corrected and I will notify NH Co-Op to connect service.

Time 0.6

08-31-09	Permit 2008-58, 184 Willow Brook Road. Dave called and said they took care of the issues with the temporary power. I went by and the entrance cable was clamped up the tree and a metal plate was installed over the unused circuit breaker positions. I notified NH Co-Op that it was ready to connect up the temporary electrical service.

Time 0.6

04-25-11	Permit 2010-44, 184 Willow Brook Road. I went to inspect the framing as requested by Dave. We discussed his plans for permanent power and the routing of his plumbing vent. The water closet will be on the front wall and he wants to route the vent pipe through the wall which is about six feet away. I told him that would be okay.

Time 0.4

08-31-11	Permit 2010-44, 184 Willow Brook Road. Dave called to have me inspect the electrical service installation so NH Co-Op will connect power to the meter panel. He used schedule 80 in the trench, backfilled with sand, and the trench is deep enough. The meter panel with the disconnect is near the bottom of the driveway and the conduit is mounted on the pole. I will notify NH Co-Op.

Time 0.5

10-27-11	Permit 2011-44, 184 Willow Brook Road. I did the final electrical rough in inspection as well as the rough in plumbing and he wants to start installing sheetrock on some of the walls. We discussed the clearances required for the wood stove that will be installed and they were okay.

Time 1.3

02-01-12	Permit 2011-44, 184 Willow Brook Road. Met with Dave to do a final inspection. Everything was completed but the deck for the front and side of the house. The door had boards across it until the deck was completed. I will issue a ninety day occupancy permit so he can stay there.

Time 0.8

05-01-12	Permit 2011-44, 184 Willow Brook Road. Deck completed along with stairs. Looked okay and I will issue an Occupancy Permit.

Time 0.4

David H Lersch

Plainfield Building Inspector