Robbie Williams

373 Route 120

469-3954

Permit # 2017-28

Map/Lot 203/21

electrical service 1000' buried and rest on poles

281 Route 12A

06-18-17	Permit 2017-28, 281 Route 12A. I inspected the trench for electrical power for the log home at the top of the hill. There will be a transformer pad at the top near the house. Robbie still needs to trench to the house from where the pedestal will be located. Conduit has sand above and under it and it i okay to backfill. He wanted to get to covered before the rain tomorrow.

Time .06

06-29-17	Permit 2017-28, 281Route 12A. I inspected the pedestal up by the house and the trench from there to the house with the conduit installed. I also inspected the transformer base he installed with the ground rods and ground loop, and the conduit terminated in the base. He left it uncovered so Liberty could inspect if they wanted. I notified Liberty via email that the site was ready for inspection. No wire pulled yet and still has about 12 feet of conduit to install down by the utility pole. Also poles down to 12A along side of driveway not set.

Time 0.9

07-07-18	Permit 2017-28, 281 Route 12A. Missing report of when installation was inspected with all conduit and cables installed. Verified house circuit panel that was now a sub panel had the neutrals and grounds isolated.

I will issue a belated Certificate of Completion.

Time 0.1

David H Lersch

Plainfield Building Inspector