Bart Industries, Inc.

Robert Baylor Industries

14 Spencer Drive

Bellows Falls, Vt 05101

802-463-9440

Permit # 2017-89

Map/Lot 210/10

360 Route 12A

Distribution warehouse

12-16-17	Permit 2017-xx, 360 Route 12A. I sent a text to Robert as I haven't heard from Osgood. He sent a text with Todd Osgood number 558-1150 and Patrick StPierre 542-2789. Sent a text to Patrick, no response as of this evening. Robert said they would be ready for a footer inspection either Tuesday or Wednesday. Robert said if I don't hear from them, let him know. Let Brad know, sent him emails with names and phone numbers.

12-19-17	Permit 2017-xx, 360 Route 12A. Received a text from Patrick that he dropped of the prints. I went on to email and downloaded and printed drawings. They may be ready for the footer on Thursday, Will let Brad know.

Time 0.2

12-21-71	Permit 2017-xx, 360 Route 12A. Talked to Brad about his inspection of the footer forms. He had some questions about the gravel parking, looks like no room for shrubs. Also wondered if building was in the correct space as per planning board. Forms okay.

Time 0.2

12-21-17	Permit 2017-xx, 360 Route 12-A – Bart Industries. Foundation: Footing Pre-pour 				inspection. Met concrete sub on site. Footings formed per plan. Rebar per plans. 				Bricked. Noted calcium chloride sprinkle in/around footing. Blankets covering 				forms for expected weather. Noticed grade stakes at tree line indicating edge of 				gravel. Not much room for evergreen hedge called for in zoning site plan 					approval. Will follow up w/Steve.

01-04-18	Permit 2017-89, 360 Route 12A. VIA email I downloaded permit application and 				supporting documents and printed.

Time 0.2

03-11-18	I'm meeting Bart's plumber @9 this morning for sub-slab plumbing. As of

yesterday he had not pressure tested the drain waste lines. He was going to 	cap them this morning before I get there. I can swing by later today to 	confirm pressure holding, but I think they may be pushing to pour the slab. 	If a <24 hour test is not acceptable can you let him know?

(I'll be unreachable in a few minutes)(there is no water to the building yet)

I can send updates tonight. Brad

03-22-18	Permit 2017-89, 360 rte 12-A – Bart – Electrical rough-in pole to meter 			box in preparation for Liberty cut-over. Met electricians on-site. Meter 			enclosure installed w/grounds (no load center yet) underground trench 			from pole covered (no-one called for inspection – by liberty?), Risers to 			meter box w/slip joints looked fine. Materials by pole for run up. Inside 			the shell was insulated (no rough-in to inspect before covering according 			to electrician email) Electricians were in the process of fishing wires 			through insulation/vapor retarder. Some of the interior stud frame 				partitions were up. Electricians thought they would be finishing rough-in 			this week and would call for inspection before covering.

03-23-18	Permit 2017-89, 360 Route 12A. Talked to Brad about inspection for 	electrical at Bart. Walls insulated, service entrance ready for hook up, but

no inspections done for trench and conduit. Sent a text to Bob about no

inspections. He said he would contact the electrician. Email from 	electrician with pictures of trench, tape, backfilled. He also said rough 	wiring would go over the insulation that was installed. I told him I would

notify Liberty. Down loaded pictures from email. Emailed Liberty that it

was okay to 	energize electrical service.

Time 0.3

04-03-18	Permit 2017-89, 360 Route 12A. Met with Robert to look over site. He

wanted to know fire rated doors were needed. I told him one from the 	office area to the garage should be rated. He said he had several exit doors. 	According to print only one outside door from office to outside that goes

right past door to garage. When I looked at the site he had added another

exit directly across from the one on the print near bathrooms and office,

away from the door to the garage. Some rough in electrical was 	completed.

Time 0.6

04-04-18	Permit 2017-89, 360 Route 12A. Received a call from electrician to do the 	rough in inspection. Looked okay.

Time 0.5

04-16-18	Permit 2017-89, 360 Route 12A. Received a call from plumber to inspect

the rough in plumbing in the bathrooms and mechanical room. All looked

okay. They were installing sheetrock.

Time 0.4

04-28-18	Permit 2017-89, 360 Route 12A. Inspected the concrete forms with crosshatch of rebar all supported for the loading/unloading area on south side of building. Looked okay and notified Robert it was okay to pour. He said it was scheduled for Tuesday.

Time 0.4

06-08-18	Permit 2017-89, 360 Route 12A. Received a call from electrician to do a final on his work and while I did the final plumbing inspection. Everything was okay. I will have to do a building final inspection when they are ready.

Time 0.7

06-27-18	Permit 2017-89, 360 Route 120. Robert called to do a final inspection on the building. Everything is completed except the interior doors. He is having problems with the size they sent. Should be fixed tomorrow. He still has some site work to block view from neighbors. I will mention that on the Certificate of Completion.

Time 0.6

David H Lersch

Plainfield Building Inspector