Liz Guaraldi

462 Willow Brook Road

496-3670 cell

Permit # 2018-01 for house repair

Permit # 2017-87  for temp housing trailer

Map/ID #215/5

11-24-17	Permit 2017-xx, 462 Willow Brook Road. The house was getting new shingles and the membrane that was on the roof came off during the storm we had with lots of wind and rain. The roof is just boards with gaps between and the water soaked the insulation, flooring, etc. Inspected the temporary electrical hook up to the mobile home. Some of the ceilings exposed and sheetrock and insulation was removed. Some electrical fixtures had water pouring out of them during the storm. The electrical wiring looked okay, no damage that I could see, but wasn't a very neat install and probably some of it was added later. The house is set up as two living spaces with the kitchen area divided into two kitchens. The insurance adjuster has been out and is coming back as they found more areas that have damage, also mildew is forming on underside of roof boards. Liz wondered about the wiring and I told her they could replace switches, lights, outlets without having to update to current code, but if they start rewiring , then it would have to meet code. She would like to have a separate electric service for the apartment. I suggested since the main panel is in a shed in the back yard and is buried to house to two sub panels that the apartment could have aerial service from the pole to its own meter and main panel. That would involve rewiring the whole house.

They will call when the sewage and water lines are connected.

Time 1.5

12-28-17	Permit 2017-xx, 462 Willow Brook Road. Liz called and said she was applying for a permit. She is using Bernie Hutchkins and will be having spray foam insulation and some interior work but no electrical.

Time 0.2

02-23-18	Permit 2018-01, 462 Willow Brook Road – Horse Farm (Guaraldi). 			Wednesday / Friday – Met Bernie Huckins on-site for upper level 				Electrical / Plumbing rough-in prior to insulation/sheetrocking. 				Upstairs/downstairs interior completely (minor exceptions) gutted to 			framing with some new interior partitions for Duplex (pre-existing use? 			Permitted?). New framing in exterior walls upstairs for new egress 				windows and new door to planned deck. Bernie indicated that he planned 			to use lags to attach deck. (Do you ask for mnfr lit on hardware to ensure 			size, quantity, pattern selection meets code?) Existing floor joists attached 			to center carrier with hangars. Hangars attached w/various fastener types, 			including some roofing nails. I mentioned it to Bernie. Maybe they should 			add some fasteners? They have sprayed insulation on the underside of the 			roof  and exterior walls (upper level only so far) (What should be the 			required thickness)? New upstairs plumbing connects to existing work in 			lower level. DWV pressure test observed on both units (one each visit). 			Upper level electrical also ok (Bernie seems to plate everything in a 2x4 			wall). Apparently there were 2 services? I believe Bernie indicated that 			they were eliminating 1 service. There is a new load center in the 				“apartment” which I understand will be a sub-panel for the new single 			service entrance in the lower level. Smokes in each bedroom.  There was a 		gas fireplace operating on my second visit – not sure if this was temp heat 			or permanent. Does Bill Taylor inspect this? How does he get notified?

David H Lersch

Plainfield Building Inspector