Nick and Amada Piper

PO Box 124

252-2669

Permit #2017-63

Map/Lot 202/8.1

New modular home

570 Old County Road

09-12-17	Permit 2017-63, 570 Old County Road. I inspected the panels mounted on the pedestal for the electricity and the wires from the pole to the pedestal.

I notified Liberty Utilities that is was ready to connect.

Time 0.6

11-01-17	Permit 2017-63, 570 Old County Road. Inspected the footer forms with rebar supported, tied, bent around corners, as Dave wanted to pour tomorrow. Looked okay.

Time 0.4

11-16-17	Permit 2017-63, 570 Old County Road. Pete called to have me inspect the foundation ICF (foam blocks that get filled with concrete) wall forms. All rebar installed tied to vertical rebar. Okay to pour.

Time 0.5

11-29-17	Permit 2017-63, 570 Old County Road. Pete called to have me inspect the footer forms for the attached garage. They will have a four foot frost wall poured. Forms and rebar okay, told Pete they could pour.

Time 0.6

12-2-17	Permit 2017-63, 570 Old County Road. Phone call with Brad about his inspections on 12-1-17  Electrical trench from pedestal to house okay.

11-30-17	Permit 2017-63, 570 Old County Road – Underground Service – Pedestal to 				house. Called Pete Danen. He said I should just stop by. I did. No-one was there 				at the time. Trench was already backfilled. The end of the trench at the foundation 			excavation was still exposed, showing conduit runs and marker ribbon. Native 				soils are very sandy and were used for backfill.

02-29-18	Permit 2017-63, 570 Old County Road – (modular new home) I met with

Peet Danen to inspect attic space prior to blow-on insulation. Observed

electrical “plug” connections and noted a couple of un supported romex

runs stapled across truss struts (~30” spans). I suggested that the owner

consider providing some protection since they were in the path the 	insulation sub would naturally follow dragging the hose. Explicitly noted

that this was a “nice to have” not a “must have”

code deficiency. Also noted one side of a romex feed amongst a group

of plug connectors in the first floor faming, that did not have a plug on it.

Owner indicated that he had had to remove the connector to feed the wire

through a framing member. I later realized that the plug might not be able

to be re-installed, allowing the connection to be inaccessible later. I called

Peet to let him know that if the connector was not intended to be re-made

on-site, that they would have to use a junction box and make it accessible

from the living space.

08-03-18	Permit 2017-63, 570 Old County Road. Met Pete to do the final inspection.

The house is modular with a attached garage with a loft that was stick built. All the plumbing was completed with the exception of the relief valve pipe to the floor on the water heater. The fitting was there but not the pipe so he hasn't done it yet. The garage wall against the house had sheetrock installed but on each side of the loft to the roof sheathing didn't have any. The loft had studs installed on the sides but the end against the house was open to the house roof. Told Pete they need to build a wall and sheetrock as well as the walls on either side of the loft walls. I will issue a CO after I verify that these issues were taken care of.

Time 0.9

09-21-18	Permit 2017-63, 570 Old County Road. Met with Nick and Pete to verify that the sheetrock was installed to the roof and in the loft that the wall was build and had the sheetrock installed to the roof. The joints and screws were covered with compound. I will issue the CO.

Time 0.7

David H Lersch

Plainfield Building Inspector