Sara Burbee

644 Route 120

558-2253

Permit # 2009-46 replaced by

Permit # 2009-65

Permit 2011-49

Map/ID # 245/1

New roof

Complete Renovation

10-14-09	Permit 2009-46, 644 Route 120. Stopped by and talked to contractor. The rear addition was torn off, just the slab there, will be building a new addition. the second floor walls were removed due to poor construction (no header over windows, etc.) and the new walls were built and sheathing installed. The front half of the first floor will be an office with a door into the shop. The inside shop walls were covered with wood panels (OSB). A beam in the apartment side from the front to rear is bad and will be replaced with a laminate beam. There is a laminated beam there for the roof that will go from side to side and the roof trusses. I told him he needed to use fire code sheetrock on both sides of the wall between the apartment and the shop all the way up to the roof sheathing. They were going to cover the wall with metal over the wood. I also said that they needed to fire code sheetrock the office walls and the ceiling which is wood. I said they would need smoke detectors in the shop, office and apartment all connected together.

Time 0.6

10-21-09	Permit 2009-46, 644 Route 120. Met with John to go over renovation of building. The shed that as on the back has been removed and the new unheated section will be twice as large as the original concrete pad. The rear of the building never had a footer poured under part of the wall. They have installed forms and will be pouring a footer to support the rear wall plate. They are putting new siding on the building and found rotten plate on the right wall. This will be repaired before installing new siding. In the shop the new door will swing out. The building will be rewired as it has wire nut splices exposed and wires not supported properly. The meter will be moved to the left corner of the building and will have a buried service entrance from the pole. The wood interior will be covered with metal. The wall against the apartment will have fire code sheetrock installed up to the roof sheathing on both sides and the office will have fire code sheetrock installed. The apartment side door will be a window and the new entrance will be at the rear. John is planning on only one bedroom upstairs.

Time 0.9

11-17-09	Permit 2009-65, 644 Route 120. Went by to see progress. No electrical yet but meter panels mounted to outside of building. Rear porch over new apartment entry almost finished, new replacement beam from front to rear to support second floor joists installed. Working on front porch that continues around corner to right side of building.

Time 0.6

11-19-09	Permit 2009-65, 644 Route 120. Dropped off the Oil Burning Equipment permit to have John fill out and get signed by Dave Best. They are working to get all outside work completed before the weather turns cold, then they will concentrate on the inside. Some plumbing work was done in moving the toilet location upstairs and a shower stall was set in place.

Time 0.5

12-1-09	Permit 2009-46, 644 Route 120. I received a call from Joe (electrician) to

inspect the buried service entrance so NG can change service from aerial

to buried. Metal conduit was only about 8’ feet up the pole and should be

10’ and cables are not long enough to reach transformer. I left Joe a

message and he called back and said he thought he did it as requested by

NG. I told Joe I would look up on the web page for NG and find out what

was needed. After reviewing the web site I called NG to verify what I read. The conduit by electrical code needs to be at least 10’ up the pole and the wires need to go to the transformer, no splices. I called Joe and let him know what I found out. He will extend the metal conduit and will pull new cables with enough coiled at the pole to reach the transformer.

Time 1.4

12-14-09	Permit 2009-46, 644 Route 120. Inspected service entrance again, okay except that conduit is a little over nine foot and Joe said NG was okay with that. I also looked at the rough in wiring and some plumbing that was completed. Looked okay.

Time 0.3

03-11-10	Permit 2009-65, 644 Route 120. I inspected the inside of the garage section. The walls are finished in metal vertical siding and the electrical wiring will be surface mounted in conduit. The upstairs has all the sheetrock installed.

Time 0.2

07-13-11	Permit 2009-65, 644 Route 120. Met with contractor to go over the layout of the mechanical room and to discuss the rest of the work that needs to be completed. The panel is placed with the required clearance and the furnace will not be in the way. A renewal permit is being filled.

Time 0.7

09-08-11	Permit 2009-65, 644 Route 120. When I was driving by I noticed they were working on the building. I inspected the walls they were constructing to close in the back porch. I also looked at the boiler installation, that was going to be oil fired so I gave them the permit to fill out for the Fire Chief. They were cleaning out a lot of old materials to the large dumpster. I let them know that Sarah should file a renewal for the permit and they thought she had. Things looked okay.

Time 0.4

03-08-12	Permit 2011-49, 644 Route 120. Sara called and said she was ready for the final inspection. There were a few ceiling fixtures not installed and some switches that needed to be mounted in electrical boxes and wall plates installed. Also she needs to have a stair railing installed to the second floor and to have the Fire Chief sign off for the oil fired boiler and I will issue an occupancy permit.

Time 0.6

.

02-14-13	I also went for a final CO inspection at 644 Rte.120 with Sara Burpee.All the electrical has been completed and the railing to the 2nd floor of the apt. has been installed. All systems there are working. I'm not sure if the Fire Chief has inspected the boiler yet. There was a door handle to be installed on the door which goes to the oil tank room, but Sara said it would be installed before anyone occupies the apartment.

I'd say the two projects are ready for CO's.

Time 0.5   12 miles

Take care,

Win Spencer Jr.

02-17-13	Permit 2011-49, 644 Route 120. I will issue a CO and email to Town Hall

Time 0.3

David H Lersch

Plainfield Building Inspector