Kevin and Victoria Ramos-Glew

PO Box 251

Meriden

469-3332

Permit # 2015-45

Map/Lot 215/18

24x40 2-1/2 story single family home

65 Jenny Road

12-21-15	Permit 2015-45, 65 Jenny Road. I received a call from Dave that he had

the footer forms ready for inspection. I told him to take pictures as I was 			out of town. Today I went by and met Dave to inspect the wall forms. 			Looked okay, extra rows of rebar on the 10' high walls on the backside.

Time 0.4

01-19-16	I took a drive to see how things were progressing at the houses on Jenny Road and Main Street. No change since last visit. Foundation and floors have been poured at Main Street, Walls were poured at Jenny Road.

Time 0.4

04-07-16	Permit 2015-45, 65 Jenny Road. All framing was completed and 3 inches 			of foam insulation was installed for basement floor that was at ground 			level. No one on site.

Time 0.4

05-16-16	Permit 2015-45, 65 Jenny Road. Doug called to have me inspect the rough 		in plumbing. Looked okay, some of the electrical was installed.

Time 0.8

07-06-16	Permit 2015-45, 65 Jenny Road. Went by to see progress. Most of the 			sheetrock was installed except for the rafters. I called the contractor and 			let him know that I never was called for a rough in electrical or insulation 			inspection. I told him I needed to meet with the contractors, Set up a time 			with Stoney Electric to meet me at the house. I talked to the insulation 			contractor, same one who done Franklin's house. I could see some areas 			that exposed the insulation in the walls and the three inch for the basement 		walls

Time 0.7.

07-11-16	Permit 2015-45, 65 Jenny Road. Met with Stoney Electric and inspected 			the electrical. All the required CO and Smoke Detector wiring was in 			place. There were some wires for receptacles and switches that were 			coiled in the ceiling waiting for the wall to be built, except they built it and 		never called him to do the wiring. He will have to fish the wires and 			mount boxes. One area on basement wall they will have to box in the 			switches. There were not any breakers installed yet and the cables were 			not installed for the buried service to the garage and the meter panel was 			not installed yet.

Time 0.4

07-14-16	Permit 2015-45, 65 Jenny Road. Went by to see if they were ready for 			Liberty Utilities. No t ready.

Time 0.5

07-27-16	Permit 2015-45, 65 Jenny Road. Stopped by to see progress on electrical 			service entrance. Meter panel installed with one 200 ampere 240VAC 			disconnect, wires up the left front of the garage to the head near the peak. 			The cables were in the conduit from the meter panel to the house panel, no 		breakers installed yet. All is okay to have Liberty Utilities come and 			connect power to new service when the electrician is ready. I will let 			Liberty know it is okay to connect when the electrician calls.

Time 0.3

08-06-16	Permit 2015-45, 65 Jenny Road. I went by to see progress, locked up but 			saw the number 2 copper cables from the panel to the junction box on the 			I thought the cables were installed last time I was there but Stoney Electric 		called and said they just installed the cables. I just needed to verify and I 			am sure I saw the copper wires installed on the last visit.

Time 0.6

09-06-2016	Permit 2015-45, 65 Jenny Road. I did a walk through to see if enough was 			completed for a Temporary Certificate of Occupancy. The panel needs 			labeled, the propane boiler installation needs finished as well as the 			radiators need to be installed, the bathrooms need to be finished, flooring 			needs finished and some trim, etc.

Time 0.4

09-08-2016	Permit 2015-45, 65 Jenny Road. Drew up the TCO.

Time 0.2

04-11-17	Permit 2015-45, 65 Jenny Road. In response to my letter I was called to do 		the final inspection of their house as they only had a Temp. CO. 				Everything was okay except that two of the three stairs the hand rails did 			not meet code. Just a 2x4 mounted to the wall, no clearance and did not go 		from top to bottom steps. All the stairs had a landing and on the upper 			stairs no railing was installed as well as the third set of stairs no railings at 			all. I will be sending her a letter with the code requirements and she will 			call when the work is completed. 3-1/2 inch width for handrails exceeds 			code width.

Time 0.5

06-30-17	Permit 2015-45, 65 Jenny Road. No response as of this date, will close 			permit without CO.

08-23-18	Permit 2015-45, 65 Jenny Road. Victoria called and said the railings were 			installed, also about three weeks ago contractor called and said they would

be installing the hand rails. Inspected the hand rails and they met code. I

Will issue a Certificate of Occupancy.

Time 0.4

David H Lersch

Plainfield Building Inspector