George & Linda West

67 Kenyon Road

675-9381

Permit # 6026

Permit # 7039

Permit # 2008-74

Permit 2009-80

Permit # 2010-72

Permit # 2012-04

Permit # 2013-03

Map/Lot 261/12

Replacement of Post & beam Home

Installation of solar electric system

10-8-08	Permit 7039, 67 Kenyon Road. I received a call form electrician Walt Smith to inspect the new service to replace the temporary service. I went over to the house and inspected the meter panel and ground rods. One of the rods was almost horizontal due to ledge. It looked like the basement was being occupied and I didn’t have any record of any inspections there and nothing from Tom to indicate he was there. The house is framed up although some windows are not installed yet. I will call George and Linda tomorrow as well as talk to Walt as to how he is going to connect meter to existing circuit panel.

Time 0.5

10-9-08	Permit 7039, 67 Kenyon Road. I called Linda at work, 802-674-2444 e 101 to find out what has been going on and to see if anyone ever inspected their house. She said she thought I was there when they poured the floor although I don’t recall ever being there although I remember talking to them in 2006. They are living in the basement until they get the house finished which took fifteen years for the last one. I set up an appointment to inspect the house tomorrow around four PM. I also notified NH Co-OP it was okay to connect permanent service.

Time 0.3

10-10-08 	Permit 7039, 67 Kenyon Road. Met with Linda and George. The basement is in two sections, a two car garage and the living quarters. It has a living room area, a bedroom, bathroom, and kitchen. It has radiant heat and tile floor. The walls are all closed up except one section where I could see most of the plumbing and some of the wiring. They have monitored smoke detectors in the bedroom and the living area. I noticed the windows were too small for egress and I asked them if the bedrooms was going to stay a bedroom when the upstairs is completed and George said yes and maybe the living room area will be made into a bedroom. We discussed the lack of inspections and I couldn’t remember the window sill height and theirs was 51 inches, looked high and I thought the code was 54 but not sure, I would check when I got back home and checked the book. I told them I couldn’t issue a temporary CO with life safety violations and the window would have to be changed. George said he could put in one like upstairs that looked like a double hung but opened like a casement. I got home and checked the codes and the sill height is 44 inches, called and left a message to that effect. The window sills are marble and the basement walls are foam blocks filled with concrete and will have to be cut to lower the windows. I will check with them next week if they don’t call me back as they shouldn’t be living there without a CO or a temporary and I let them know if they had a fire, etc that the insurance company may not cover the loss without it. If they don’t respond I will have to issue a letter stating that the home is in violation of life safety code with a copy to the Fire Chief and the town.

Time 0.9

10-23-08	Permit 7039, 67 Kenyon Road. Met with George and inspected new service entrance and discussed the temporary occupancy permit. The electrical service was okay and George will be putting an egress window in the bedroom in the basement. If he goes down to the top of the concrete wall the sill height will be okay. He said he could special order a window to fit and meet the requirement. I told him I would issue a six month temporary which would be valid as long as the window was installed within sixty days.

Time 0.5

11-19-09	Meeting with solar contractor for West house. They needed the second floor finished to install equipment on end of house that has the service entrance and electrical panel. In looking for another location they wanted to install the disconnect switch on the right end of the house but they need to have a permanent deck in place so you could reach the switch. I also told him they needed a separate permit for the solar and cannot be part of the existing permit to build the house.

Time 0.8

01-07-10	Permit 2009-80, 67 Kenyon Road. Inspected the solar installation including the panels, inverter, batteries, and the disconnect switch (mounted next to the electrical meter on the other side of the house from the solar equipment. George also replaced the window in the basement bedroom to egress size and has a temporary platform to meet the forty-four inch sill height. I will issue temporary CO’s for six months at a time. He also has all the windows installed upstairs and has sprayed foam insulation.

Time 1.3

01-24-11	Permit 2010-72, 67 Kenyon Road. I received a call from George to have me inspect the rough in wiring on the mail floor and some recessed lighting on the lower level. All the wiring was done on the exterior walls and a sub-panel was installed on the first floor. I let him know that he needed the new child-proof receptacles and the arc fault circuit breakers that are now required. He asked if he needed to sheetrock the walls first as they want wood walls, this also applies to the ceiling.  let him know that he could use a fire retardant sealer instead of using sheetrock behind the wood. He thought that would be great idea and will do that.

Time 0.6

08-24-13	Permit 2013-03, 67 Kenyon Road. After doing the final inspection of their garage under another permit, Linda asked whether they could use tongue and groove boards on the walls as they are getting ready to insulate. I told them it needed to be coated with a fire retardant or it needs ½ inch sheetrock. They are going to use boards with a fire retardant.

Time 0.4

David H Lersch

Plainfield Building Inspector