Kimball Union Academy

PO Box 188

Meriden

469-2152

Permit # 2016-31

Map/Lot 104/1 104/4

17 Bed Dorm new apartment rear of existing building

26 Main Street

06-21-16	Permit 2016-31, 26 Main Street (KUA). Went to inspect the footer forms and they were not ready yet, barely half way.

Time 0.4

06-22-16	Permit 2016-31, 26 Main Street (KUA). Inspected the footer forms with rebar all installed. Gave the okay to order concrete.

Time 0.5

06-30-16	Permit 2016-31, 26 Main Street (KUA). Inspected the wall forms and installed rebar for the dorms. Looked okay to pour.

Time 0.8

07-11-16	Permit 2016-31, 26 Main Street (KUA). Inspected the backfill of the foundation and looked at the pictures for the perimeter drains that were installed last week. Looked okay and went to daylight.

Time 0.1

07-20-16	Permit 2016-31, 26 Main Street (KUA). Inspected the newly poured concrete floor and the framing on the lower side as well as the sills  top of the foundation. Looked okay.

Time 0.4

07-26-16	Permit 2016-31, 26 Main Street (KUA). Inspected the 400 ampere service entrance and the rough in electrical in a new wall as well as some lighting circuits in the house. They also had the sprinkler pipes installed.

Time 0.3

07-28-16	Permit 2016-31, 26 Main Street (KUA). Inspected the new 400 ampere circuit panel and service entrance cable from meter panel disconnect. I will email Liberty Utilities later tonight that it is ready to energize.

Time 0.6

08-02-16	Permit 2016-31, 26 Main Street (KUA). I did a walk through with contractor of the new dorms inspecting the electrical connection and plumbing connections between the units. Looked okay.

Time 0.6

08/31/16	Permit 2016-31, 26 Main Street (KUA). Went to Meet Electrical State Inspector Art at 10AM. He wasn't there but I walked through the dorm halls and basement. Electrical wire should have been metal clad no romex, that was the reason to meet with Art as well as a full inspection. They are finishing up the sprinkler system, some of it is in operation.

Time 0.5

08/31/16	Permit 2016-31, 26 Main Street (KUA). Received a call from Art, he is in Lebanon and on way. The area between joists that have the wiring will have sheetrock installed and the junction boxes will be moved so cover is accessible. We inspected the panels and Art pointed out some minor issues that weren't correct but he would let go. I will have to follow up to make sure all romex wiring is covered with sheetrock. Have to check on the two MC main cables that feed the panels in the basement of the dorms have certified MC connectors. A/C units in the rooms need to have the disconnect switch next to the unit. Also dorm rooms need to have at least four receptacles. I told them I could issue a temporary CO so they could finish those items. The Fire Chief Frank and the State Fire Marshall will issue a permit to occupy based on life safety codes.

Time 0.8

08/31/16	Permit 2016-31, 26 Main Street (KUA). Electrician called Art after getting into the dorm rooms. The disconnect switches were located in the closets and they were not going to have doors. Art said it was up to me as to what needed to be done. I was called and went back to look at the dorm rooms and I felt that a plastic label on the A/C unit pointing out where the switch was located and a red wall plate on the switch in the closet next to the A/C. Based upon where you stand you can see the unit and the switch. The rooms have several sets of quad receptacles at least four single receptacles.

Time 0.8

09-06-2016	Permit 2016-31, 26 Main Street (KUA). Dropped off Temporary Certificate of Occupancy.

Time 0.1

09-29-16	Permit 2016-31, 26 Main Street (KUA). I inspected the basement where they closed in the electrical wiring by sheetrock between joists. Saw label for modular units in kitchen of apartment unit. Labels on A/C unit and red wall plates for disconnect switches not installed yet. Once that is verified, I will issue a Certificate of Occupancy.

Time 0.5

10-27-16	Permit 2016-31, 26 Main Street (KUA). I inspected the labels on the room units specifying where the disconnect switch was located and the red wall plates on the switches. I will issue the Certificate of Occupancy.

Time 0.4

David H Lersch

Plainfield Building Inspector