Kimball Union Academy

PO Box 188

Meriden

469-2152

Permit # 2018-22

Map/Lot 105/31

Full Renovate

51 Main Street

08-06-18	Permit 2018-45, 727 Route 12A

Hi Dave,

Re: KUA health center in section. – I met w/Jason on-site. This was 		my first visit to the site and I’d seen no drawings for the project at 			that point. The interior had been gutted and new interior partitions 			were in place. The exterior walls had new metal stud walls installed 			inside the existing masonry walls to provide for new insulation and 			electrical. They had neglected to call before spray foam insulation 			was installed on the exterior walls and ceiling.  I was able to see 			framing, electrical and plumbing rough-in the interior partitions. 			Jason walked me through the project and apologized for not calling 			for the inspection at the right time.

The new wiring is bx, and what I could see appeared reasonably 			well installed. Most of the new branch circuits appear to run to a 			sub-panel located on the main floor. There was a new entrance 			panel (not installed at the time) to replace the existing main in the 			basement. They are not planning to change the location of the main 		entrance. The new service will be 200a and there is currently a 			conduit from the building to the pole at the street. There was new 			pex water supply lines and pvc dw&v piped to a new bathroom and 			various exam rooms, and all looked good. I did suggest air sealing 			at penetrations and around window jambs, which Jason said they 			would take care of. There are new windows throughout, which 			Jason said he believed meet egress requirements (worth checking 			on drawings). I did not see any indication of bath fans or other 			mechanical ventilation. Jason indicated that there will be a dropped 			ceiling which would allow for ductwork, but that he would check with 		Hunter to see what is planned. I believe that the energy code calls 			for controlled ventilation and that the building code calls for 				mechanical ventilation for health care facilities (perhaps not of this 			scale/type?).

I think that’s it, but let me know if you have any questions. I did 			speak with Jason, Doug and Hunter about improving 					communication to avoid the last minute/too late call for inspection. 			They each assured me that it was not deliberate, and that they 			would do better.

Regards,

Brad

08-23-18	Permit 2018-22, 51 Main Street. Met with Doug to go over the renovation. Brad was there on 8/6 and I don't have his written report yet, just phone call of status. Sheetrock installed. Doug will keep me in the loop.

Time 0.5

09-11-18	Permit 2018-22, KUA 51 Main Street. Met with Doug to do a final inspection of the front part of the clinic. Life safety alarms, detectors, lights installed through out building. Items need completed were flooring in the two bedrooms and two bathrooms, and exam room. It will be a special vinyl that goes up wall about six inches and all corners are sealed. This is needed to contain any fluids, etc. This work should be completed this week as they want to move in equipment and furniture this week and have staff in there on Monday. The office area in the front is okay now to occupy and I will have the Completion Certificate completed to give Doug on Friday when I verify floors are installed and toilets are installed in the two bathrooms.

Time 0.8

09-14-18	Permit 2018-22, KUA 51 Main Street. Stopped in to see progress, still had the two bedrooms with baths and the exam room to finish the flooring.

Will stop in Monday to give Certificate of Completion.

Time 0.2

09-17-18	Permit 2018-22, KUA 51 Main Street. Dropped off Certificate and looked over work that is completed, everything finished except floors in two bedrooms.

Time 0.3

David H Lersch

Plainfield Building Inspector