Kimball Union Academy

PO Box 188

Meriden

469-2152

Permit # 2013-22

Map/Lot

Miller Hall renovation

57 Main Street

08-06-13	Permit 2013-22, KUA Miller Hall 57 Main. I inspected the footer forms on the west side of Miller Hall. Looked okay and I told them they could pour. Talked to contractor and Doug Plummer from KUA.

Time 0.2

08-08-13	Permit 2013-22, KUA Miller Hall 57 Main. Inspected the footer forms on the east side of the center section of Miller Hall. Looked okay.

Time 0.4

09-26-13	Permit 2013-22, KUA Miller Hall 57 Main. I inspected the foam insulation (3”) on the second floor walls of Miller south (rear of building). I also inspected the foam insulation (8”) on the roof sheathing and the sprayed fire-proof coating over the insulation. I inspected the electrical rough in conduit and the greenfield in the second floor classrooms in Miller south. I also inspected some of the steel framing on the first floor and for the second floor of the learning center, as the second floor will be poured tomorrow. The hole for the stairs to the second floor by the three classrooms will be cut out as soon as the rest of the steel work is completed downstairs.

Time 0.6

10-03-13	Permit 2013-22, KUA Miller Hall 57 Main. I inspected the foam insulation (3”) on the first floor walls of the learning center of Miller south (rear of building). I inspected the electrical rough in conduit and the greenfield on the first floor in the learning center. I also inspected the rough in electrical on the first floor walls that were going to have sheetrock installed.

Time 0.2

10-17-13	Permit 2013-22, KUA Miller Hall 57 Main. After the contractor meeting I inspected the fire retardant on the steel in the path for egress. I also inspected more electrical wiring as well as the rough in plumbing for the two bathrooms. The outside of the new concrete block walls for the learning center addition were being sprayed with two inches of foam prior to having the bricks installed.

Time 0.4

10-24-13	Permit 2013-22, KUA Miller Hall. I went to attend the contractor meeting that was supposed to start at eleven. No one was at the scheduled place. I checked around at the other places the meeting would be, no help. I couldn’t get in touch with Doug. I was asked if I needed help and after explaining, he finally got a hold of Cliff (general contractor) and I was told the meeting was at 11:30.  I went to Town Hall now instead of after meeting. Went back for meeting, still no one there. After unsuccessful attempts to find anyone or the meeting, I inspected the insulation on the outside of the learning center that was all completed and they were getting ready to start laying the brick.

Time 1.4

10-31-13	Permit 2013-22, KUA Miller Hall. I went to the contractors meeting and then inspected the rough in wiring on the second floor of the learning center.  It looked okay. This is the last rough in inspection for the permit. The insulation, electrical, and plumbing has been inspected and they are getting close to having all the sheetrock installed. They have about six more weeks to install the electrical devices, plumbing fixtures, doors, trim, and the life safety items. I will try to have Win Spenser do the final with the Fire Chief in December.

Time 2.0

11-19-13	Permit 2013-22, KUA Miller Hall. Met with Win Spenser and Cliff to familiarize him with KUA project and to meet Cliff. We walked through the site and they had most of the sprinkler system piping installed. Some of the walls are completed and painted. KUA will schedule all inspections with me, to keep me in the loop.

Time 1.2

12-05-13	Permit 2013-22, KUA Miller Hall. Win attended contractor meeting.

Time 1.5

12-12-13	Permit 2013-22, KUA Miller Hall. Win attended contractor meeting.

Time 1.0

12-12-13	Permit 2013-22, KUA Miller Hall. Read over construction meeting notes for DEC. 5th.

Time 0.2

12-19-13	Permit 2013-22, KUA Miller Hall. Read over construction meeting notes for DEC. 5th.

Time 0.2

12-31-13	Permit 2013-22, KUA Miller Hall. Performed above ceiling inspection (Win).

Time 1.5

01-23-14	Permit 2013-22, KUA Miller Hall. (Win) Miller Student Center is getting close to getting their final insp. for a CO. I may have time this week to go to their weekly meeting on Thurs.

01-28-14	Permit 2013-22, KUA Miller Hall. (from Cliff) Dave, I meet with Win yesterday afternoon for the Final inspection he is all set we are awaiting the State Fire Marshal visit tomorrow. When that is complete do you need to hear from the Fire Chief and then issue the CO?

01-30-14	Permit 2013-22, KUA Miller Hall. Received email with Fire Chief's letter authorizing occupancy for the renovated first floor, but a hold for the second floor until the punch list is completed. I issued a temporary CO for the first floor for a period of thirty days for them to finish the second floor and after Frank gives the approval, I will issue the final Occupancy Permit.

Time 0.5

02-06-14	Permit 2013-22, KUA Miller Hall. Read email-meeting minutes from

last weeks meeting.

Time 0.2

02-08-14	         Permit 2013-22, KUA Miller Hall. Email from Doug Plummer at KUA with letter attached from Fire Chief stating okay for Certificate of Occupancy.

Dave,

Here's a letter from Frank regarding the occupancy in Miller.  I asked

him to do this one today so that we can get people in the 2nd floor on

Monday.  He will send out a letter on his letterhead next week and I

will forward that to you for your records.

Doug

I created the CO and signed it, scanned it and emailed to Doug at KUA.

Time 0.6

David H Lersch

Plainfield Building Inspector