Ranji and Andrea Keen

79 Bonner Road

Meriden

469-3006

Permit # 2017-29

Map/Lot 106/3

addition / garage

06-01-17	Permit 2017-29, 79 Bonner Road. Met with Jim and Brad to inspect the 			trench and conduit from the garage to the location of the new addition. I 			gave the okay to backfill.

Time 0.6

06-14-17	Permit 2017-29, 79 Bonner Road. Brad called to have me inspect the 			footer forms for the addition, looked okay.

Time 0.5

06-26-17	Permit 2017-29, 79 Bonner Road. I inspected the ICF frost wall forms for 			the addition including the rebar. Not all blocks installed.

Time 0.5

06-27-17	Permit 2017-29, 79 Bonner Road. Brad called and said he would be ready 			to pour at 2PM. I inspected the wall forms with the horizontal and vertical 			rebar. Okay to order concrete.

Time 0.4

08-28-17	Permit 2017-29, 79 Bonner Road. Met with Jim and Brad to inspect the 			rough in electrical wiring and the new electrical panels in the house and 			the garage. Looked okay.

Time 0.5

09-08-17	Permit 2017-29, 79 Bonner Road. I inspected the insulation in the walls of 		the addition and in the ceiling of the lower level. Looked okay. Fiberglass 			in ceiling on second floor and Brad once the ceiling is installed will blow 			in loose insulation above the fiberglass.

Time 0.4

11-14-17	Permit 2017-29, 79 Bonner Road. Jim O called to have me inspect the 			trench and installed conduit from the right side of the house down the right 		side of the driveway to the utility pole. About 6 conduits, power to house 			and back to future garage location, plus for solar cables that will be on 			garage. Okay to backfill.

Time 0.4

11-20-17	Permit 2017-29, 79 Bonner Road. Brad called to have me inspect the 			forms for the garage slab. Needed some more wire mesh and bricks to 			raise the rebar. Brad said he would be sure that it was done before pouring 			concrete, they weren't finished on setting up the forms.

Time 0.4

11-20-17	Permit 2017-29, 79 Bonner Road. Jim O. called to have me inspect the 			new service entrance as the wires were run from the pole to the meter 			panel. I notified Liberty Utilities that they could connect the service.

Time 0.5

03-29-18	Permit 2017-29, 79 Bonner Road. Telephone call from solar contractor 	about inspecting solar install at 79 Bonner Road. Scheduled for Monday at 	10:30 AM.

Time 0.1

04-02-18	Permit 2017-29, 79 Bonner Road. Inspected the solar PV system addition 	on the garage roof with inverter, 100 ampere electric panel that is a sub-	panel from the house. Inspected disconnects, labels in garage and at meter 	on the house with the 200 ampere house disconnect in the meter panel. 	Time 0.5

04-05-18	Permit 2017-29, 79 Bonner Road. Received a call from solar contractor, 	they had to change the inverter in the garage and needed me there to 	inspect and sign off. Liberty was there as well as the electrician. Check 	install at the house and garage, all disconnects and labeling. Check 	shutdown of solar if lost utility power at both solar locations. Everything 	okay, gave Liberty my approval as required.                                          	Time 1.5

08-18-19	Talked to Brad several times. Someone else was going to do blown in 	insulation. Never verified it was completed, but permit work for the permit 	with Brad as contractor was completed. Issued Completion Certificate.

David H Lersch

Plainfield Building Inspector