Marianna McKim

94 Bonner Road

469-3999

Permit # 2017-19

Map/Lot 105/10

REBUILD ELL HOUSE TO BARN

05-16-17	Permit 2017-19, 94 Bonner Road. Inspected the footer forms for the new ell. Looked okay.

Time 0.5

05-22-17	Permit 2017-19, 94 Bonner Road. Inspected the wall forms for the ell. Looked okay.

Time 0.3

05-31-17	Permit 2017-19, 94 Bonner Road. Mr. McKim called to ask about the new electrical panel they want to move from the first floor to the basement next to sub-panel. I stopped by to see location they wanted to put it and the ceiling is only 68 inches high. The code requires 78 inches. They will install a backboard where the basement height is higher and meets code.

Time 0.6

06-12-17	Permit 2017-19, 94 Bonner Road. I inspected the rough in electrical for the ELL and also the rough in plumbing for the bathroom so they could insulate.

Time 0.5

06-14-17	Permit 2017-19, 94 Bonner Road. I inspected the sprayed in foam insulation. In answer to a question about fire protection between ell and barn, I told them yes to a fireproof door and one-half inch sheetrock on the wall between was sufficient.

Time 0.3

06-21-17	Permit 2017-19, 94 Bonner Road. I inspected the new aerial electric service entrance mounted on the north east corner of the house as well as the new circuit panel in the basement. I notified Liberty via email it was okay to connect to new service entrance.

Time 0.8

11-13-17	Permit 2017-19, 94 Bonner Road. I completed the final inspection of the addition between the house and the barn. Looked okay, half bathroom contains laundry, All lights, outlets working and spaced per code requirements. Smoke detector installed. I will issue a Certificate of Occupancy.

Time 0.2

David H Lersch

Plainfield Building Inspector