Plainfield School

92 Bonner Road

469-3250

Permit # 2017-45

Map/Lot 105/11

solar and new electrical transformer, replacing old one and new

conduit and cables from pole to transformer and to building.

07-25-17	Permit 2017-45, Plainfield School. Went to inspect trench for electrical work. They were just starting. They will call when ready.

Time 0.4

07-25-17	Permit 2017-45, Plainfield School. Part of the trench was ready for inspection, conduits from the pole to the location for the new primary power transformer were installed and some of the conduits from the transformer (secondary power) to the school were installed. Soil very sandy with little stones and three feet deep. It will take a couple of days to complete the trench to the school, I will inspect when I can and they will also take pictures.

Time .06

07-26-17	Permit 2017-45, Plainfield School. Inspected the base for the transformer and continuation of trench and conduit to school and some of the trench and conduit to the solar array.

Time 0.4

07-27-17	Permit 2017-45, Plainfield School. Transformer in place, Liberty working on pole, another contractor will handle the primary wiring from the pole to the transformer. Inspected more trench to school, trench to solar array filled in and clearing trees, etc. for the array. Still need to remove old transformer and install junction box in its place.

Time 0.7

07-28-17	Permit 2017-45, Plainfield School. Power disconnected, old transformer removed, trench and conduit finished to where old transformer was, forms for pad for disconnect to building ready to pour. Pouring concrete  into form for a pad for electrical box and electric meter where solar cables and building service entrance cables from transformer will be connected.

Time 0.4

07-31-17	Permit 2017-45, Plainfield School. Norwich Tech. called to have me inspect the new disconnect to the school so Liberty could connect power.

I also inspected the solar disconnect by the new transformer. Both sets of cables come from the transformer. Emailed Liberty that it was okay to connect power.

Time 0.8

09-12-2017	Permit 2017-45, Plainfield School. Stopped by to see progress. Piers set, vertical post installed, conduit continued across road to electrical panels.

Time 0.4

10-18-17	Permit 2017-45, Plainfield School. Did the final inspection of the solar array. All labels installed, at building AC disconnect switch by school, at main transformer with meter, solar disconnect panel by pole, and on the three inverters mounted on the solar array framing. All inverters operational, generating power. Signed the utility company form and will issue a Certificate of Completion.

Time 0.4

David H Lersch

Plainfield Building Inspector