Birdseye Properties, LLC

PO Box 49

675-2549

Permit # 2014-35

Map/ID # 107/17

1064 Route 12A

Connection between gallery and warehouse

04-08-14	Permit 2014-35, 1064 Route 12A. Met with owner to go over plans to construct two ramps, one from the basement to the storage building and one from the storage building to the main floor of the showroom. It would be enclosed. The only issue I had was that the only basement egress (bulkhead) would be replaced by the ramp enclosure. The egress has to go directly outside and couldn’t go into another building then exit outside. He was going to have the architect look at the problem. I suggested if they couldn’t find a way, they could make an egress window with a window well in another location.

Time 0.5

08-14-14	Permit 2014.35, 1064 Route 12A. I stopped by as I haven’t heard anything from them since the permit was issued. The footer and frost wall was poured as well as most of the building was framed with a roof over it. I let the contractor know what inspections they should have had called for. I gave him a little bit of a hard time and inspected what was completed. Discussed what they were going to do and it involved plywood on the walls for the basement egress and a knee high wall between the two walkways, one from the garage to the first floor and one from the basement to the garage that had the egress door. I let him know that that entire area required fire rated sheetrock and fire rated doors that self close and latch on the first floor entrance, the two entrances to the garage. I also told him I needed to see the rough in electrical when it was ready.

Time 0.4

08-28-14	Permit 2014-35, 1064 Route 12A. Met with electricians to inspect the rough in wiring. there will be an exit light at the bottom of the ramp from the basement and one above the egress door. There will be emergency lighting in all three sections of the connection as well as one outside the egress door. Also switches and light circuits. They will take pictures of the insulation for me to see when I get back.

Time 0.3

09-11-14	Permit 2014-35, 1064 Route 12A. I saw the pictures for the insulation while away and inspected the work completed to date including fire doors and fire code rated sheetrock. Okay.

Time 0.3

David H Lersch

Plainfield Building Inspector