Katelyn & Jeremiah Goulet

111 Whitaker

802-291-3065

Permit # 2017-08

Map/Lot 252/9

sfh

08-09-17         Permit 2017-08. 111 Whitaker Road. Telephone call about inspecting the

power trench on Friday, Called Brad to have him go by and inspect.

Time 0.1

08-14-17        Permit 2017-08. 111 Whitaker Road. Brad said they weren't ready,	conduit                                                                                                                         	laid, trench open. Not finished at transformer location. I went by to see if 	there was any progress. Still the same. Talked to owner about having sand 	over the conduit, said okay and electrician will finish when backfilled..

Time 0.5

- 08-14-17	Permit 2017-08, 111 Whitaker Road – Electrical – Trench inspection. No-one on 				site. Trench open. Conduit runs placed. No backfill. Conduit runs stopped short of 			pedestal. Additional materials nearby; ground rods, ground wire, sweeps, etc. 				Native material has some stone. Not sure what is planned for backfill, but 					probably some sand should be used to protect conduits.

08-14-17	Permit 2017-08, 111 Whitaker Road. Went by to see if backfilled, no 	change.

Time 0.3

08-15-17	Permit 2017-08, 111 Whitaker Road. Went by, no change, waiting for sand 	to be delivered so they could backfill some of the trench so the electrician 	could start pulling wires.

Time 0.4

09-05-17	Permit 2017-08, 111 Whitaker Road. I inspected the footer forms with 	rebar installed, tied together, bent around corners and down steps. Okay to 	pour. Also the trench was covered, pull box not installed and conduit tot 	transformer pad not installed.

Time 0.5

09-11-17	Permit 2017-08, 111 Whitaker Road. Inspected the walls forms, okay. He 	wants to pour a short footer and wall instead of the pier that shows on the 	drawings due to the weight, told him to go ahead. I also inspected the 	transformed pad with the conduit installed and the pedestal with electrical 	panels, also the pull station down the driveway. No cables yet but ready to 	pull.

Time 0.3

09-16-17	Permit 2017-08, 111 Whitaker Road. Call from electrician, left him a 	message that I could go Saturday and left him a message of what I found 	Monday and if that is what  he wanted me to inspect. Went and it was still 	the same as the other day. Just a further note he called 9-19 and said he 	would be pulling the wires and would be ready by Monday.

Time 0.6

09-20-17	Permit 2017-08, 111 Whitaker Road. Telephone call on Friday about 	perimeter drains. I went to inspect nothing yet but foundation was sealed.

Time 0.4

09-20-17	Permit 2017-08, 111 Whitaker Road. Jacob called and said the srains were 	ready for inspection. Looked okay to backfill. They will call when they are 		ready to pour the floor.

Time 0.3

09-25-17	Permit 2017-08, 111 Whitaker Road. Inspected the electrical service entrance from the pole, to pull box, to transformer, to pedestal with 200 ampere meter panel with 200 ampere disconnect. Looked okay except the conduit at the pole was about an inch away from the pole and clamps were installed and the top clamp held the conduit tight to the pole., need work order number and I will notify Liberty Utilities via email.

Time 0.5

09-25-17	Permit 2017-08, 111 Whitaker Road. Doug called and said the plumbing for the basement was installed and ready for inspection. Looked okay, vents, toilet, shower, sink drains to main run to outside the foundation.

Time 0.2

09-29-17	Permit 2017-08, 111 Whitaker Road. Doug called and said the basement floor had the three inches of insulation and the radiant heat plumbing installed and ready for the okay to pour the floor. I gave the okay.

Time 0.2

10-05-17	Permit 2017-08, 111 Whitaker Road. I inspected the footer forms for the attached garage. Looked okay.

Time 0.4

10-06-17	Permit 2017-08, 111 Whitaker Road. I inspected the frost wall for the garage. Looked okay.

Time 0.3

10-13-17	Permit 2017-08, 111 Whitaker Road. Inspected the trench and conduit from the pedestal to the house. It was okay except I told them it should be schedule 80 conduit under the driveway, they will change two sections of conduit. Also mentioned sand, was on site, they will add sand as they cover.

Time 0.3

10-31-17	Permit 2017-08, 111 Whitaker Road. Stopped by to see progress and find out when they would be ready for more inspections. Garage and shop area was all framed and framing the rest of the house was just starting. He figured in December the electrician will start work and it will be January or February before they would be ready for the final.

Time 0.4

12-28-17	Permit 2017-08 111Whitaker Road. Jeremiah called for a framing inspection. He will be starting on electrical and plumbing in about two weeks. I told him he could start when he was ready and I would have Brad go by when he has time.

Time 0.1

01-29-18	Permit 2017-08, 111 Whitaker Road. Received a call to inspect the rough in electrical, left word for Brad. Called again, talked to Brad about again about inspection. They asked me about fire protection between the house and garage. I let them know the wall against the house needed 1/2 inch sheetrock installed to the roof sheathing unless they were going to sheetrock entire garage.

Time 0.2

02-01-18	Permit 2017-08, 111 Whitaker Road and met with the builder (also named 			Goulet). He wants to use the garage as work space and get some heat in 			there as work in the rest of the areas proceeds. To do that they have run 			some (permanent) branch circuits to outlets and switches in the space. 			They would like to insulate the garage. Everything looked fine in the 			garage and at the main panel in the basement so I think they can cover up. 			I suggested that he take pictures and forward them to you, which he 			indicated he would do.

While there he walked me through the rest of the building, which is at the 			shell phase, dried-in – framed, wrapped, w/windows & doors, but no 			electrical or plumbing rough-in.

Let me know if you have any questions.

Regards,

Brad

05-01-18	Permit 2017-08, 111 Whitaker Road. Inspected the rough in plumbing and electrical as more was done since Brad's visit. The garage ceiling was wood panels, sheetrock was installed on wall adjoining house. The wall above the garage needs to have sheetrock installed to the roof sheathing as that is a shared wall with the house. Did an overall inspection of construction both inside and outside, looked okay.

Time 1.1

05-25-18	Permit 2017-08, 111 Whitaker Road. Inspected the insulation and the plywood [panels that were had groves for the radiant heating on both floors. He needed to fire stop penetrations. He said he would do that today. Doug was there finishing up some plumbing. He said the water and drain pipes were pressure tested. Okay to install sheetrock.

Time 0.5

10-22-18	Permit 2017-08, 111 Whitaker Road. Contractor called to have me do an inspection and had questions about getting ready for the final. Hand rails need to be installed, kitchen cabinets need installed and some still being constructed, relief valve needs discharge pipe, some doors need installed, and some other finishing items (grout around wood stove, receptacles on kitchen backsplash). Josh said they hoped to be completed in two weeks.

Time 0.8

11-09-18	Permit 2017-08, 111 Whitaker Road. I did the final inspection of the house and garage/workshop. The only thing that wasn't completed were the side panels on two of the cabinets that would be completed today. Inspected radiant heating system with wall mounted propane boiler. All smoke detectors installed and operational. About one half of the basement finished, other half storage and mechanical equipment. I will issue an occupancy certificate.

Time  0.8

David H Lersch

Plainfield Building Inspector