Richard and Elizabeth Morse

1116A Stage Road

709-7144

Permit # 2015-60

Map/Lot 240/20

renovate carriage shed to apartment

11-05-15	Permit 2015-60, 1116A Stage Road. Met with contractor to inspect the inside of the carriage shed. Wiring is not very neat, but it is not being changed. The kitchen area will have to have some new wiring to bring up to code. There will also be some plumbing. The windows upstairs on the front of the carriage house do not meet egress and since they are not being replaced and there isn't any outside work on the building they can stay. I recommended it would be safer if they did. I will go back when the rough in is ready for inspection.

Time 0.6

12-22-15	Permit 2015-60, 1116A Stage Road. I did the final inspection of the solar installation on the carriage shed that was added to the existing permit for the creating an ADU. I inspected the rough in electrical and plumbing. There were several areas where nail plates were needed and I told them since the wiring and receptacles are new that the panel needed to be brought up to code with arc fault breakers.

Time 0.5

07-22-16	Permit 2015-60, 1116A Stage Road. I was asked to do the final of the Carriage Shed. There should have been a few more receptacles in some of the rooms. The kitchen was oaky. They still didn't install the arc fault breakers in the panel. On my first visit, I couldn't get to the second floor and now I can see that the windows will meet egress as they are double swing in, which from below looked like small double hung. I will issue the CO but will hold off on mailing for a few days to see if the arc-fault breakers are installed.

Time 0.7

David H Lersch

Plainfield Building Inspector