Don & Judy Jordan

71 King Drive

675-3238

Permit # 2012-74

Map/Lot 255/6

House

163 Kenyon Road

12-06-12	Permit 2012-74, 163 Kenyon Road. This report contains several things regarding this permit. I reviewed the plans for the house prior to the permit being approved on the 28th of November. I also had several telephone calls, from Don, and a couple from Biebel Builders regarding what I needed to inspect and what I required for the footer and ground wire, and also for the trench for the buried utilities. I told them to take pictures of the footer and the trench with the conduit installed and email them to me. The walls will be of the foam blocks as per email from Paul along with the pictures I requested. Everything looked okay.

Time 0.4

12-13-12	Permit 2012-74, 163 Kenyon Road. I received an email yesterday to have the foam foundation wall inspected on Thursday so they could pour on Friday. I gave them Win's telephone numbers and I told the Paul that

if he didn't hear from him to email me pictures of the site and foundation wall forms. I review the pictures today and things looked okay and I replied that it was okay to pour.

Time 0.2

12/14 Basement form inspection for new home at Jordon residence on Spencer Road.  Okay to pour walls

12/17 I went to the Spencer Road new house to check on the status of the footing drains and the weatherproofing of the exterior basement walls. Wall weatherproofing complete, still needs some work on the footing drains.

12/18 I went to Spencer Rd. house again to see that the footing drainage had been completed and to verify that the under slab plumbing waste piping passed it's pressure test. Both of these issues have been completed and I called Jeff Potter of Beibel Builders to go ahead and proceed with covering the plumbing and to backfill the walls when they need to.

From Win Spenser's email on 12-20-12

01-02-13	Permit 2012-74, 163 Kenyon Road. Paul Biebel called to get permission to lay the last section of conduit and the sweep as Fairpoint installed the pole and wanted to backfill as it was going to get below 0 tonight. I gave the okay.

Time 0.2

03-05-13	Permit 2012-74, 163 Kenyon Road. I went by to see the progress on the house as I have been out of town for three months and I heard that they were putting in the trusses. All the trusses were in and they were sheathing the roof. They still needs some bracing on the trusses and will call me when all the framing is completed.

Time 0.4

04-09-13	Permit 2012-74, 163 Kenyon Road. Stopped by to see progress, quickly inspected some of the rough in plumbing and electrical.

Time 0.3

04-23-13	Permit 2012-74, 163 Kenyon Road. I was called to inspect the rough in plumbing. Met with plumber and did the inspection. All was okay, pressure tested as well.

Time 0.7

05-24-13	Permit 2012-74, 163 Kenyon Road. I received several calls regarding code issues from contractor. The height of the railing on the deck will be 36 inches high and the sheetrock in the garage will be installed on the house wall all the way to the roof sheathing as per codes. The attic access will be outside above the deck as the ceiling will be insulated and would eliminate the heat loss that they would have if inside the house.

Time 0.1

05-28-13	Permit 2012-74, 163 Kenyon Road. I inspected the foam insulation on both floors and around the headers and above the plates extending on to the roof sheathing. Looked good.

Time 0.4

06-12-13	Permit 2012-74, 163 Kenyon Road. Received a call to inspect the solar installation. Told them I would be there around 4PM. No one there when I got there. I inspected what I could, All the panels on the roof were mounted, electric meter installed. I will go early tomorrow.

Time 0.4

06-13-13	Permit 2012-74, 163 Kenyon Road. Electrician wasn’t there but inspected

the sheet rock that was being installed. The main floor was finished except for sanding and the lower level just needed the ceiling installed.

Time 0.4

06-13-13	Permit 2012-74, 163 Kenyon Road. Met with solar contractor and inspected the rest of the installation. Looked okay and I had him power it up. Working okay, I will sign off inspection forms for the solor installation.

Time 0.9

08-08-13	Permit 2012-74, 163 Kenyon Road. At the request of the owner, I went to do the final inspection. The original permit specified a two story house. The second floor had one bath and two bedrooms. The first floor had one bedroom and 1-1/2 baths. The basement was a finished play area. The new plans that I had them fax to me is what was built. It is a single story house with a in-law apartment in the finished basement. The main floor has and two full bathrooms. It also has a full kitchen. The finished basement has a living room with a door to the outside, a bedroom, a small playroom, a full bathroom and a den/office. It has a two car attached garage, a whole house generator with transfer switch, and a solar electric system. I let the owner that the den/office cannot be used as a bedroom as it does not have a direct access to outside. I will issue a Certificate of Occupancy.

Time 1.7

David H Lersch

Plainfield Building Inspector