David Stark

168 Croydon Turnpike

508-246-8943

Permit # 2016-49

Map/Lot 213/23

30x40 garage

08-01-16	Permit 2016-49, 168 Croydon Turnpike. Inspected the floating slab for the 		garage. Two rows of rebar around perimeter and wire mesh laid entire slab 		area.

Time 0.4

08-22-16	Permit 2016-49, 168 Croydon Turnpike. Inspected the completed garage. 			Sprayed foam insulation on the garage ceiling. The second floor will have 			blown in insulation and fiberglass in the walls. He will be having a new 			aerial electrical service from the utility pole.

Time 0.8

09-26-16	Permit 2016-49, 168 Croydon Turnpike. I inspected the electrical service entrance and it was okay, will notify Liberty Utilities. I inspected the rough in electrical wiring. The metal boxes he used should have been larger to handle two 12-2 MC cables with receptacles. Also the length of the wires in the box were short of the required length. I let him know for future reference but I didn't require him to pull all the cables and replace wiring and boxes. He had all the insulation installed as well.

Time 0.5

09-27-16	Permit 2016-49, 168 Croydon Turnpike. Notified Liberty Utilities via email service is ready to connect.

Time 0.2

David H Lersch

Plainfield Building Inspector