Guy Champagne & Ruth Grover

20 King Drive

469-3060

Permit # 2014-63

Map/Lot 252/28

Garage 28x28x12

08-07-14	Permit 2014-63, 20 King Drive. Guy called and said he was building a garage and the slab is already poured and some framing is already completed. He called when he found out he needed a permit and the permit needed inspections. Guy said the slab was six inches thick and used wire mesh in the slab. Not sure how it was supported prior to pouring concrete. I told him he should have installed two rows of rebar around the perimeter, supported and wired together. The weight of the building is on the edges and without rebar the concrete may crack due to the weight. Not according to code. He asked me to come by and inspect what he has completed. Two car garage with 12’ walls and Lavalley’s is building the roof trusses. I told him that the floor may crack due to the weight of the walls on concrete reinforced by wire mesh only.

Time 1.0

08-25-14	Permit 2014-63, 20 King Drive. Guy called and wanted me to inspect the 			rough in electrical for his garage. It was all constructed and Lavalley 			trusses installed and roof. Door and windows installed. The meter panel 			was installed and the circuit panel and boxes, etc. His wires were too short 		according to code, requires 6" length of wire outside the box. He also just

twisted the grounds in the box without a wire nut. He didn't apply no-oz to 		the aluminum service entrance wires in both the panel and the meter panel. 		His ground wire was not continuous from the panel to the two ground 			rods, but was clamped together. I told him he needed to fix those items 			except for the boxes that didn't have the 6" of wire as he would have to run 		all new wire. I told him he also needed to call the power company to 			schedule the hook up. After I do an inspection tomorrow to see if these 			items were taken care of I will notify NH Co-Op that it is ready to hook up 		service.

Time 0.6

08-26-14	Permit 2014-63, 20 King Drive. I went over to see if Guy fixed the code 			problems with the electrical. He put wire nuts on all ground connections in 		the electrical boxes, No-ox applied to aluminum entrance cables. Ground 			wire was continuous from the circuit panel to both ground rods. Before I 			went there I was at the town hall and Steve didn't have a permit for Guy. I 			called Guy and told him I thought you applied for a permit. He said he 			gave it to his son to deliver. I told him the permit can't go forward until the 		application is at least at the town hall with a drawing of the dimensions, 			etc. I also let him know again he needed to contact the power company. 			After I got home I pulled out the NH Co-Op's code book. Guy should have 		called to have them come out and see what needed to be done for the new 			service. I emailed Bruce at the power company and let him know what I 			found. I am sure that the meter panel does not have a disconnect as 			required by them, also I don't think that he has three feet of wire at the 			head as well. It is had to judge as the walls are 12' high. I asked Bruce if 			he could meet me there tomorrow as I am getting ready to go out of town.

Time 1.0 with code and email.

09-25-14	Permit 2014-63, 20 King Drive. Inspected the new meter panel with the 			disconnect circuit breaker. Looked okay except he still had EMT for the 			conduit to the head and it should have been ridged conduit. I notified 			Brian at NH Co-Op via email. He responded via email the next day and 			said Guy installed the ridged conduit and they had connected the electrical 		service.

Time 0.6

David H Lersch

Plainfield Building Inspector