Jordan Casey Green & Samantha Jane Davidson

288 Platt Road, Cornish 03745

675-2327

Permit # 2014-07

Map/Lot 259/13

garage addition that contains an den, office space and space for two cars.

addition is over the line in Plainfield

05-20-14	Permit 2014-07, 288 Platt Road. Inspected the trench and conduit for the new buried electrical service that will replace the aerial service. They need to install the meter panel after closing in the window of the house that the new service will enter.

Time 0.4

05-29-14	Permit 2014-07, 288 Platt Road. Inspected the service entrance and meter panel that was installed to move aerial service to buried service in preparation for the new addition.

Time 0.3

06-24-14	Permit 2014-07, 288 Platt Road. Received a call from contractor to inspect the footer forms at three PM. I went to inspect and the concrete truck was there and pouring. The forms looked okay except there wasn’t any rebar in the falls (changes in elevation of the footer) and they just used a piece of rebar for the ground instead of copper wire. I told them they should not pour until it was inspected and I was told they would be ready by 3PM. He was a little upset that I had him install the missing rebar so all the rebar would be connected together. He just wanted to wet set them.

Time 0.4

06-30-14	Permit 2014-07, 288 Platt Road. I inspected the forms for the foundation walls. They were almost finished, running a little late, some of the rebar was installed correctly. Let them know when they were ready they could pour.

Time 0.6

07-23-14	07-24-14 Telephone calls regarding 62 Pierce Road, 241 Freeman Road, 40.5 Hayward Road and 288 Platt Road.

Time 0.5

07-29-14	Permit 2014-14, 288 Platt Road. Inspected foam insulation on foundation wall and pictures of foam and radiant heating plumbing on part of the floor that was poured. They will call later this week when the garage section is ready to inspect the same items before pouring the garage floor.

Time 0.4

08-07-14	Permit 2014-7, 288 Platt Road. Went by to inspect the trench for the power and propane line as well as the hole for the buried propane tank. Hole was ready and were putting sand in the bottom before putting the tank in the hole. Sand will surround the tank once it is in the hole. Trench was just getting started. Will go tomorrow morning.

Time 0.2

08-08-14	Permit 2014-07, 288 Platt Road. I inspected the trench from the tank to the left front corner and the trench from the tank to left front corner of the existing house. Plenty of sand and separation between the electrical conduit that was previously buried and the propane line.

Time 0.2

08-15-14	Permit 2014-07, 288 Platt Road. I did the rough in electrical inspection and it was okay. The next inspection is for the insulation.

Time 0.3

08-21-14	Permit 2014-07, 288 Platt Road. Inspected the rock wool insulation in the walls and the spray foam insulation in the ceiling. Looked okay.

Time 0.3

David H Lersch

Plainfield Building Inspector