Tracy Sandmann

36 Jenny Road

469-3160

Permit # 2012-03

Map/ID # 224/21

Renovate barn to guest house

03-26-12	Permit 2012-13, 36 Jenny Road. I inspected the drain pipes in the trench that was cut in the concrete floor for the bath, etc. drains. Looked okay and they will be covering with sand then laying radiant heat pipes before pouring a concrete floor on top. They will call when the radiant pipes are laid.

Time 0.4

04-23-12	Permit 2012-03, 36 Jenny Road. I inspected the radiant heat pipes and blue foam board floor insulation. Pipes pressurized and were okay.

Time 0.5

06-28-12	Permit 2012-03, 36 Jenny Road. I inspected the rough in electrical wiring. It was okay except for some places that needed metal plates due to the wires that were less that 1-1/4 inch from the edge of the studs.

Time 0.6

David H Lersch

Plainfield Building Inspector