Patricia J. Murray

37 Sugar Hill Road

443-2072

Permit # 2016-56

Map/ID # 256/14

Ground mounted solar array, tracking.

09-08-2016	Permit 2016-56, 37 Sugar Hill Road. I was called to inspect the 				installation of the pre-cast base for the ground mounted solar array and the 		trench for the A/C cables from the array to the house electrical panel. They 		weren't ready and should be ready later today. Base had to be set before 			trench dug.

Time 0.3

09-08-2016	Permit 2016-56, 37 Sugar Hill Road. I was called to inspect the 				installation of the pre-cast base for the ground mounted solar array and the 		trench for the A/C cables from the array to the house electrical panel. The 			large pre-cast base was installed and the cables were in the trench from the 		array to the house along with the coax control cables. The mail pole was 			mounted with the inverter and electric meter. The large hole needs to be 			filled in as well as the trench then the solar panels can be installed.

Time 0.3

09-12-16	Permit 2016-56, 37 Sugar Hill Road. Solarflect called and said they are 			ready for the final inspection. When I got there they were trying to upright 		the solar array to bolt the two sections for the mounting. Wench wasn't 			working, either the battery or the wench. I waited but it wasn't going to be 			ready. Also labels weren't installed.

Time 0.3

09-13-16	Permit 2016-56, 37 Sugar Hill Road. Solarflect called and said they are 			ready for the final inspection and when I got there the system was 				operational. They still didn't put the labels on and told me they would. 			I signed of on the form when Mark said he would pick them up and put 			them on, I will verify tomorrow. I will issue the Completion Certificate.

Time 0.4

David H Lersch

Plainfield Building Inspector