Louise Richards

421 Willow Brook Road

276-0004

Permit # 2015-02

Map/ID # 224/17

Renovation after water/mold

02-12-14	Permit 2015-02, 421 Willow Brook Road. I talked to contractor about the work that is going to be done after the house was gutted due to water and mold. Insurance company doesn't want to pay for any upgrades but according to Larry Davis the roof rafters are not large enough to support the snow load, there were skylights that were installed without a permit after talking to Michelle, wiring is a combination of old knob and tube, etc. and needs to be upgraded. A new panel was installed when the two car attached garage was built by Larry (NOTE: No inspections were preformed, letter sent, no response.) The exterior walls won't support the thickness needed for the new insulation, some are not even 2x4's. I asked Win to call Larry and do a walk and let me know what he thinks. I feel to be able to issue a CO it needs to be up to code. As of 2-21 Win hasn't got with Larry in response to my email yesterday as to status of inspections to date that I have requested.

Time 0.4

02-27-14	Permit 2015-02, 421 Willow Brook Road. (Win) Meeting with contractor at 421 Willow Brook Rd.

Time 0.75

03-24-15	Permit 2015-02, 421 Willow Brook Road. I received a call to do the 			framing inspection. The first floor was supported by a new beam and 			posts, the old studs on the left side of the house were removed and 2x6's 			installed. New walls were framed up upstairs and a beam was across the 			dormer that had the rafter cut. Front roof was raised and supported as it 			needed raised. Cross ties were installed on the rafters. Framing around the 			skylights was reinforced. Looked okay. They will call when ready for the 			rough in inspection.

Time 0.5

04-01-15	Permit 2015-02, 421 Willow Brook Road. I completed the rough in 			electrical and plumbing inspection. I also did a final inspection of the 			attached 1-1/2 story garage so I could do a completion certificate for that 			permit. On the right side two new curved walls were constructed at the 			entry and the bathroom was gutted.

Time 0.8

04-15-15	Permit 2015-02, 421 Willow Brook Road. Met with contractor to inspect the insulation installation. Fabric installed over studs and on joists over part of the kitchen and filled with cellulose. I told them they could install sheetrock.

Time 0.8

10-15-15	Permit 2015-02, 421 Willow Brook Road. The entry way with the curved walls came out great. I inspected one bathroom on the right of the house that just had new fixtures installed and the gutted bathroom was completed. They poured a cement floor for the basement under the section that was gutted. The upstairs had two bedrooms and a bath and a half. The windows in the bedroom were there before renovation and do not meet egress codes as to size and sill height. Since there wasn't any work to the house framing or siding they weren't touched. I will issue a CO.

Time 0.8