Brandon William LaHaye

45 Porter Road

252-1781

Permit # 2017-49

Map/Lot 216/2.1

new sfh modular

06-19-17	Permit 2017-49, 45 Porter Road. Met with home owner to go over questions about the electrical trench as it will be aerial part way then buried. Covered depth, sand requirements, spacing between low voltage conduit and power conduit. Also covered footer requirements.

Time 1.0

06-27-17	Permit 2017-49, 45 Porter Road. I inspected the trench with the conduit installed, good base of sand, 3 feet deep, gave the okay to backfill.

Time 0.5

08-18-17	Permit 2017-49, 45 Porter Road. I inspected the footer forms for the modular home. Looked good, rebar supported, bent around corners, tied together, center supports not pads but a footer through the center. Contractor ordered tie down strips that some modular home manufacturers require on the four corners. House corners tied to foundation wall. Okay to pour.

Time 0.8

08-23-17	Permit 2017-49, 45 Porter Road. I inspected the wall forms, looked okay to pour.

Time 0.5

08-25-17	Permit 2017-49, 45 Porter Road. Inspected the perimeter drains, looked okay. Discussed foundation insulation.

Time 0.8

08-30-17	Permit 2017-49, 45 Porter Road. Inspected the plumbing in the basement floor and the blue foam insulation along the walk out wall so they could pour the basement floor.

Time 0.4

09-13-17	Permit 2017-49, 45 Porter Road. Inspected the power trench from the pedestal to the house. Looked okay.

Time 0.7

09-25-17	Permit 2017-49, 45 Porter Road. I inspected the connections inside the house on the main panel and the pedestal with the meter panel and 200 ampere disconnect. Grounds and neutrals were separated in the house panel. I will notify NH Co-OP that they can connect from the pole to the meter panel on the pedestal.

Time 0.5

11-10-17	Permit 2017-49, 45 Porter Road. Inspected the first and second floors All smoke and co detectors installed. Needs front steps, balusters on deck and stairs on right side entrance. In basement plumbing drains connected, septic ready and waiting for state inspection. Propane wall mounted boiler installed correctly, water connections made, high flow pressure pump with small pressure tank. Stairs to the first floor need steps and railing. Electric panel all connected to house circuits. Getting close.

Time 0.6

11-27-17	Permit 2017-49, 45 Porter Road. I was asked to do an inspection so they could move in the house before it was totally finished. All the heating, electrical, plumbing was completed. Items needed for a CO is building rear deck and front porch, installing hand rails to the basement and the second floor, finish installing siding, finish installing insulation in basement, and covering approved septic system along with some landscaping. I will issue a Temporary Certificate of Occupancy until I get back in the spring.

Time 0.9

09-28-18	Permit 2017-49, 45 Porter Road. Brandon called me to do the final inspection. Siding all installed, landscaped just recently, rear deck built with stairs on the left side of house, and front porch built. I will issue a CO.

Time 0.6

David H Lersch

Plainfield Building Inspector