Steve & Katy Sheehan

598 Stage Road

675-2352

Permit #2008-76

Map/Lot 254/2

Garage into porch, mud room, pantry, 12x12 shed addition

11-05-08	Telephone calls

Permit 2008-76, 598 Stage Road.

Talked to Tom Lappin about project. Concrete contractor already poured slab for 12x12 shed addition without letting me or Tom know. Tom will call when framing is completed. The rest of the project will not be started yet.

01-06-09	Permit 2008-76, 598 Stage Road. Tom called to have me inspect the work converting the garage and adding the shed addition on the rear of the garage. I inspected the electrical that the home owner was doing himself. Tom took me over the wiring including the relocation of the generator cable and the new sub panel in the garage. The only problem I found was that the sub panel needed to have a ground bar installed and the neutral and grounds separated and a ground wire and rod installed.

Time 1.5

David H Lersch

Plainfield Building Inspector