Mark Hardy

18 Ann Lee Road

Harvard, Ma 01451

978-772-6101

Permit # 2010-71

Map/Lot 214/20

60 True Road

04-16-11	Permit 2010-71, 60 True Road. I met with the general contractor Chris at the town hall to go over the plans for the new house.

I verified the plans called for egress windows in the bedrooms and we discussed the inspection schedule.

Time 1.0

05-06-11	Permit 2010-71, 60 True Road. Chris called to have me inspect the footer

forms and the ground wire. All rebar was supported, bent around corners,

continuous rebar in the falls (step in footer), and ground wire secured to

rebar in footer. The next inspection is the wall forms and then the perimeter drains in answer to Chris’ questions.

Time 0.6

05-10-11	Permit 2010-71, 60 True Road. I inspected the wall forms and everything was okay for them to pour the concrete.

Time 0.8

05-16-11	Permit 2010-71, 60 True Road. I inspected the perimeter drain pipes, the stone and the mesh covering and the drain to daylight. It was okay and I told them they could backfill.

Time 0.5

06-07-11	Permit 2010-71, 60 True Road. I inspected the trench and conduit from the pole by the road up to the foundation. Looked okay, sand available to backfill on site. I mentioned that NG requires a metal sweep at the pole.

Time 0.7

06-17-11	Permit 2010-71, 60 True Road. Inspected the meter panel and exposed conduit at the house and the pole. They still didn’t have the conduit on the pole above the sweep. Also when going through the house I noticed that the basement did not have any means for a direct egress to outside. I called Chris and left message.

Time 0.5

06-24-11	Permit 2010-71, 60 True Road. I had several calls from Chris and the electrician about the house. The electrician didn’t want to install a disconnect at the meter that is required because of the distance to the electric panel that is on the adjacent wall in the basement. The electric cables would be too big for the lugs in the 200 ampere meter panel. They would work on a solution as I told them they needed the disconnect. Chris called and we discussed the egress requirement and I told him it is new with the 2009 IRC. They are still working on a solution and I gave him some possible solutions. Chris called the other day and said they would be ready for the inspection for the electric so National Grid would connect power. Chris called today and said they were ready for the electrical inspection and I asked about the solution to the disconnect. He said they used copper cable instead of aluminum wire which is smaller but a lot more expensive. I told Chris that Win Spenser would do the inspection and if it was okay I would notify National Grid.

Time 0.7

Hi Dave, I went to the house on Sandborn Road yesterday(6/24/11). The kitchen countertops have been installed and the house appears that it's ready for occupancy. The final landscaping and steps haven't been done yet, but the house overall appears to be completed. The temporary steps are in place and there are no railing on them at this time. I also went to the house being built on Jenny Road. No one was there, but I looked at some of the service aas I couldn't get into the basement. If the power company is Nat. Grid, I don't believe that they'll accept the PVC conduit on their pole. They require rigid pipe with a bonding bushing and a length of appropriately sized ground wire that can be bonded up the pole to the neutral connection or a driven ground rod at the base of the pole. I also didn't see any driven ground rods by the meter disconnect area. Would need to schedule a time to meet the electrician to go over these issues. Win Spencer

06-26-11	Permit 2010-71, 60 True Road. Win,

THE CONTRACTOR CHRIS SAID THEY TALKED TO MEL SO I DON'T KNOW WHAT HE TOLD THEM.

I TOLD THEM THEY NEEDED SCH80 UP THE POLE AND RECOMMENDED THEY GO ON LINE AS THEY WERE HAVING TROUBLE

GETTING A HOLD OF NG.

CHRIS' NUMBER IS 802-369-6003, ALSO THE ELEC. IS NOW FROM NH OR VT.

THANKS DAVE

06-28-11	Permit 2010-71, 60 True Road. I talked to Chris about the electrical service and if they were all set with Mel at National Grid. They were ready for NG to connect power at the pole. Also Chris told me that he didn't feel the code requires an egress from the basement. I told him it was in the code and since he wanted to discuss it further when I get home I told him I required the egress regardless of what he thought the code said.

I notified National Grid that it was okay to connect power.

Time 0.5

07-14-11	Permit 2010-71, 60 True Road. I inspected some of the rough in plumbing, and we discussed installing plumbing through a beam along the stairs that does not have a wall upstairs and a wall will be built under the beam in the basement. It looks like it should be okay. We also went over the basement egress plans and they will have a door to the outside with fire code sheetrock installed and a fire rated door to the garage at the top of the stairs.

Time 0.8

08-18-11	Permit 2010-71, 60 True Road. I received a call from Chris about meeting him to go over some items. I left a message and didn’t hear back so I went over to see how things were going. No one was there but I inspected the rough in plumbing and electrical wiring that was completed. Everything looked okay except there are quite a few places that will have to have metal plates installed where the plumbing goes through the plates. I also tried to call Chris again and his voice mail box was full.

Time 0.7

09-09-11	Permit 2010-71, 60 True Road. I stopped by to see how things were progressing. The electrician thought in another week he would be ready for the rough in inspection. The plumber was there and should be ready about the same time.

Time 0.8

10-04-11	Permit 2010-71, 60 True Road. I met Chris to go over the items that needed to be completed prior to installing the rest of the insulation. They were not supposed to install the insulation prior to the rough in inspections. The electrician still had some work to do and there wasn’t any issues with his work. The plumbers need to put metal plates where the pipes are closer the 1-1/4 inch from the edge of the framing. I pointed out several of the locations to Chris. I also told Chris that the water and sewer pipes need to be pressure tested yet. Chris will let me know when I can do a final rough in inspection, it will not be easy as most of the insulation is installed, but it is un-faced and just laid in the walls.

Time 1.0

10-20-11	Permit 2010-71, 60 true Road. Chris called to have me inspect all the rough in. Metal plates were installed where needed and most of the walls were insulated except where they pulled out to install the metal plates. The plumber still hasn’t pressure tested the lines yet and I let Chris know that it would have to be done. He is going to have the sheetrock installed and if there is a problem with the pressure test it will be the responsibility of the plumber to repair any walls that he needs to open.

Time 0.7

11-11-11	Permit 2011-71, 60 True Road. I stopped by to see how things were going. No one was there, pressure gage on drain pipe and showed no pressure. It looked like all the ends were plugged. Sheetrock was there but nothing was installed. (NOTE: I went by on the 17th to go to 82 True Road and noticed that there still wasn’t any one there)

Time 0.5

12-13-11	Permit 2011-71, 60 True Road. Met with the plumber and inspected the rough in plumbing that was under pressure. They were still doing the radiant heat plumbing as well as installing the boiler. The first floor is radiant and the second floor is hot water baseboard. Looked okay.

I also met with the contractor that was going to install solar electric panels. After several telephone calls about the disconnects, since the inverted will automatically disconnect the solar panels and the inverted output to the electrical panel in the event power is lost, I told them they didn’t have to install a disconnect switch, as per their request, at the meter, but I did request that they post two signs, one at the meter and one at the panel stating the automatic disconnect.

Time 0.9

02-09-12	Permit 2010-71, 60 True Road. I met with solar contractor to inspect the solar electrical installation as well as look at the solar hot water installation that was still in progress. they had a plastic red sign on the main house disconnect stating the solar disconnect is inside on the inverter. Although the code specifies the disconnect should be at the service entrance, since the inverter disconnects the panels if the utility voltage is low and also disconnects the inverter from the utility power if utility power is lost. They took pictures of the installation and were going to send them to National Grid for their approval. I approved the installation.

Time 0.9

05-11-12	Permit 2010-71, 60 True Road. I met the solar contractor to inspect the solar hot water installation. The system was up and working and I didn’t see any problems with the system, but the HW boiler needed a pipe on the relief valve and the hot water tank’s relief valve was dripping as well as two threaded connection on the pipes. Just a note to file that I have left two messages to Chris about the expired permit. I looked over the rest of the house while I was waiting for the contractor.

Time 1.0

David H Lersch

Plainfield Building Inspector