Tim Longacre and Kimberly Cunningham

54 Westgate Rd #10 PO Box 336

675-2257

Permit # 2014-66

Map/Lot # 221/2

28x48 sfh

626 Route 12A

10-02-14	Permit 2014-66, 626 Route 12A. Met with Tim at the house site and they were going to start with the foundation next week. Dave B. is the concrete contractor and will be calling me for the footer form inspection.

Time 0.4

10-10-14	Permit 2014-66, 626 Route 12A. Inspected the footer forms and there were okay.

Time 0.6

10-14-14	Permit 2014-66, 626 Route 12A. I inspected the trench with 6 inches of sand under the conduit. Tim is going to put about a foot of sand on top due too pieces of ledge that was taken out.

Time 0.7

10-21-14	Permit 2014-66, 626 Route 12A. Inspected the foundation wall forms with the rebar installed. The trench was filled in to where they stopped and you could see the sand under and on top of the conduit. Looked good.

Time 0.3

10-30-14	Permit 2014-66, 626 Route 12A. I inspected the electrical pedestal, the conduit into the basement and the two sets of wires. They changed from 100 ampere service to 200 ampere service and used two, two inch conduits with wires for 100 ampere each for a total of 200 ampere. I also inspected the basement drain plumbing and the perimeter drain pipe from the foundation to daylight. The perimeter drains around the foundation will be done later by Scott.

Time 0.5

11-02-14	Permit 2014-66, 626 Route 12A. Inspected the perimeter drains, foundation insulation. Okay

Time 0.4

12-4-14	Permit 2014-66, 626 Route 12A. Win met with Tim and inspected the framing and told him to call when the plumbing and electrical were roughed in prior to installing any insulation.

Time 0.75

01-21-15	Permit 2014-66, 626 Route 12A. Win did the rough in electrical and plumbing inspection. Gave the okay to insulate and sheetrock.

Time 1.0

02-05-15	Permit 2014-66, 626 Route 12A. Win completed the insulation inspection and gave the okay to sheetrock.

Time 0.5

03-31-15	Permit 2014-66, 626 Route 12A. Met with Tim to do a walk through to see what still needed to be completed. Cabinets being installed, propane boiler installed, Doug Freeland installing air handler, all trim installed. Still need light fixtures installed as painting just completed. Told Tim he would need hand rails on the stairs to the basement.

Time 0.7

04/30/15	Permit 2014-66, 626 Route 12A. Tim dropped by when I was at Red Hill as he recognized my truck. He wanted a final inspection of his house. He was on the way to work and we scheduled a 5PM inspection. The house was completed except for the siding on the front which Tim was doing. The inside was all completed and meets code. I will issue a Occupancy Certificate.

Time 1.2

08-06-15	Permit 2014-66, 626 Route 12A. I stopped by to see the progress on the porch. It was basically completed and looked okay.

Time 0.3

08-20-15	Permit 2014-66, 626 Route 12A. Tim had asked me to come by and I told him after I came back from Pa. We scheduled that Saturday but I was in DHMC Friday night for a week and a half. We scheduled today. He fired his electrician and hired a new one to finish. Not sure when this occurred.

The original plan was to have a 100 ampere service. After the two 2 inch conduits were buried, he decided he wanted 200 ampere service. I talked to the electrical and Tim and since they ran two inch pvc conduit that the only way to use what they had was to run copper wires, which they said would be too expensive. The electrician wanted to know if he could run two parallel runs to the house in the 2-two inch conduits that were buried. I checked the problem out with reliable source. They could run one set of wires for the 240vac 100ampere in one conduit and another set of 240vac 100 ampere in the other conduit. The wires have to be the same length and the be clamped at both ends so you would double the ampere of the total run.

I check this out with Tim and that was the way it was completed. One of the issues I had was number 2 wire was used for the service entrance cables and that is only good up to 150 feet, the total run from the pole to the house was close to 300 feet, way too far for number 2, it should have been at least 1/0 wire. I told Tim I would draft a letter with my findings.

Time 0.9

David H Lersch

Plainfield Building Inspector