Mountain Valley Treatment Center

PO Box 325

Orford, NH 03777

353-9102

Permit # 2017-68

Map/Lot 238/8-9

Renovation caretakers house to offices

addition to carriage house

703 River Road

09-21-17	Permit 2017-68, 703 River Road. Met with Pilot Construction's Nate and Deane to go over plans for the renovations that were planned and talked about the carriage house addition. 200 ampere service is at the caretakers house that will be offices and nurses office and that should be sufficient, only 100 ampere service at the carriage house and will probably have to be upgraded. They want to remove the entrance so they can start the footer for the addition. I told them the will need certification from a fire protection engineer that it meets life safety codes. I told them they may need a fire suppression system, but not sure, the engineer would know.

They will give me plans for the electrical and plumbing when they are ready. They will call when the footer is ready for inspection.

Time 1.1

09-28-17	Permit 2017-68, 703 River Road. Had a meeting with contractor, electrician, and architects to go over plans. They are going to leave wall and add fire rated door on the first floor to separate the stairs used for egress coming from the second floor. Exit and emergency lighting will be installed as well as smoke and CO detectors. Do to under fifty people they said they didn't need to have sprinklers installed and doors didn't have to open outward. Glass entrances and side panels will be tempered glass. New deck were replacing the stone steps on the front two entrances and will have emergency egress lighting. They are waiting for the concrete contractor to form the footer for the addition of the gate house.

Time 1.3

10-03-17	Permit 2017-68, 703 River Road. Deane called to have me inspect the footer forms for the addition on the gate house. Looked okay. Also looked at some changed plumbing in the basement and went over plans to remove two walls next to stairs to second floor, bearing walls. Temporary walls built and going to install some manufactured beams to support the top of the stairs on the second floor. Need to do that so wall can be built to enclose stairs from the second floor for egress.

Time 0.9

10-06-17	Permit 2017-68, 703 River Road. Inspected the frost wall for the addition on the gate house. Looked okay.

10-10-17	Permit 2017-68, 703 River Road. Gate house-inspected the poured frost wall and went over what they are planning for the slab on the front of the house. Putting in a footer and concrete wall under lip of house slab between the new frost walls and a short wing on either side of the frost wall to sure up the edge of the slab. Caretakers house-Inspected the new beams they put in to handle the load that was on the two short supporting walls on each side of the stairs to the second floor. Looked good. Inspected the plumbing for the sewage pump and plumbing for the small bathroom in the basement.

Time 1.0

10-13-17	Permit 2017-68, 703 River Road. Inspected the rough in plumbing in the addition to the carriage house so they could prepare the floor for concrete.

Time 0.8

10-17-17	Permit 2017-68, 703 River Road. Inspected the prep. work to pour the floors for the Carriage house addition. Looked okay. Deane and I discussed how he was going to meet insulation value which will be greater that required. Inspected some of the rough in electrical wiring at the caretakers house and went over locations for emergency and exit lighting. Should be ready next week for final rough in as planning on foam insulation on Wednesday.

Time 1.1

10-26-17	Permit 2017-68, 703 River Road. Met with electrician and Deane to go over rough in electrical and plumbing. Electrical and plumbing looked good. Fire Chief was there and they are going to install a monitored alarm system in with detectors, strobes, pull boxes, etc. for both the house and Carriage house. Had a call earlier in the week from the architect and we discussed the alarms, wanted to use battery ones in old section of carriage house. I said that they need to be hard wired and all connected together between the old section and the addition. I also let him know that we needed the stamp from the Fire Protection Engineer as to alarms and emergency lighting. I suggested he contact the fire chief. That is probably the reason they went with a monitored alarm system. I told Deane to call Fire Chief to see if he wants to see the rough in alarm locations and wires and I said I would contact him to see if we can go together on the next visit and definitely on the final inspection.

Time 1.4

10-30-17	Permit 2017-68, 703 River Road. Met with Deane to inspect the closed cell sprayed foam insulation. Basement walls, roof rafters, and first and second walls that had sheetrock removed. Looked okay to install sheetrock.

Time 1.1

11-02-17	Permit 2017-68, 703 River Road. Deane called and asked me to stop by. He said Bill and the State Fire Marshal was there and looked at all three buildings. Deane told me they have to close in the mechanical area with one hour sheetrock and a fire rated door as it is open to the basement. He said that the Carriage House needs to have fire suppression installed. they want to have stamped drawings for the alarm and suppression system. Deane showed me the bathroom in the Carriage House and said they were going to make it ADA. Toilet needs 42" width and there is the wall on the left that has the main drain pipe. Except for a few inches from the back wall to enclose the pipe, the rest of the wall will be moved to the left for the new handicap shower that will be installed. The required width of the toilet area will less than required and will not extend beyond the toilet tank. Only change will be that the grab rail above the tank will not be 42 inches. He also mentioned an additional sprinkler head needed to be installed in the crawl space in the kitchen in the Inn and no decision on whether the main stairs needs to be closed off.

Time 1.0

11-17-17	Permit 2017-68, 703 River Road. Met with Deane to inspect the framing at the carriage house. Looked okay and they were going to start the rough in electrical and plumbing. The alarms will be tied to the main fire alarm panel in the main building. At the office building ( caretakers house) there will be alarms, etc. but at the present time it will not be monitored. The sheetrock is installed and the conference room downstairs was supposed to have glass windows on each side and you could see the exit signs at both exits. Now they will be putting an exit sign in the header over the entry to the room on the right when coming out of the room. They are hoping on being completed in early December. I let Deane know that I will be issuing a Certificate of Completion for the caretaker's house. It will state the scope of the work for the permit and will specify that only that building has been completed and inspected.

Time 1.5

- 12-01-17	Permit 2017-68, 703 River Road (Home Hill) Inspection: Carriage house addition, 			Electrical & Plumbing Rough-in. Met Dean on-site and reviewed work area. New 				work was neat / orderly and appeared complete, Questions arose about ventilation 			for IAQ, make-up air for bath fans. Worker volunteered that gas heat units had 				their own air ducts (sealed combustion kits?) Dean said he would ask owners 				about plans for mechanicals. Dean walked me through the older section of the 				carriage house and described plans to move oil tank and install tanks for sprinkler 				system. He also showed / explained planned work in stairwell and existing 				apartments. I raised question about use/definition of stairwell as egress path with existing single ½ drywall. Dean indicated he would look into issue and get back to us. Dean brought me through the admin building. I observed the existing service entrance was not in an easily observed location and did not have a disconnect. Dean responded that the entrance was existing and scope of 				current work did not include work on the service. He agreed that the location was 				not easily seen and less than ideal. He indicated that they were already planning 				new signage to identify buildings and that he might suggest the owners add a sign 				to identify the service location. -

12-06-17	Permit 2017-68, 703 River Road. Talked to Brad and Deane about inspection. There are disconnects on the Inn and the carriage house but none on the Headquarters Building. There were not any changes to service entrance on that building. In the carriage house (dorms) the walls were 1/2 inch sheetrock which wee okay with the installation of the fire suppression system. Brad brought up the issue asking if lead paint was used. The pump for the fire suppression system needs backup power and also the alarm system needs to have power in the event of a loss of power. Brad also wondered if an R-3 classification was the correct one.

Time 0.8

12-11-17	Permit 2017-68, 703 River Road. Brad inspected the foam insulation at the dorms (carriage house) and several areas only had about an inch and a half. Called Deane and let him know. He will have the guy come back and redo the areas that need more. I will reschedule Brad.

- 12-11-17	Permit 2017-68, 703 River Road – Insulation.  Pre-wall close-up. Met Dean on-				site. Spray poly-iso insulation depth varied considerably. Agreed with Dean to let 				Dave decide whether it was sufficient. Otherwise coverage was thorough – I went 				into the mechanical “loft” and checked “hard to reach” areas and they were well 				insulated, as were corners and intersections. I later learned that Dean had his sub 				spray additional material in shallow areas, I returned to complete the inspection. 				Significant improvement.

12-12-17	Permit 2017-68, 703 River Road. Brad went back and everything was okay.

12-14-17	Permit 2017-68, 703 River Road. Deane sent a text that the fire suppression pipes were ready for inspection so they could sheetrock.

I sent back I would schedule Brad and Bill also. Deane responded that Bill was there and inspected the pipes. I called Brad and left a message.

12-15-17	Got a hold of Brad. I told Brad that Bill should have seen if you could have gone with him or have let us know that he inspected the system pipes and it was okay. Brad will call and let me know as there isn't any reason for Brad to go if it is okay with Bill. Brad called me back and said Bill said that it was okay. I sent a text to Deane that they could cover if no additional work was done since Brad's last visit.

01-12-18	Permit 2017-68, 703 River Road. Received texts from Deane about a final inspection for the Headquarters building with Brad and Bill Taylor for 9AM on Wednesday and an inspection of the alarm system at the Carriage House. He will email me the drawing and one to Bill of the system. Sent a text to Brad and also forwarded him the texts from Deane. Talked to Brad and sent him via email the drawing. Brad will get with Bill and confirm with Deane as they want the electrician there as well.

Time 0.3

01-17-18	Permit 2017-68, 703 River Road. Brad called and said he and Bill inspected the Headquarters Building and the Carriage House. They inspected the alarm system and the fire suppression system. There were four issues at the Headquarters Building, some fire topping, etc. and will send pictures of the fixes, after I make sure all is okay I will issue a Completion Certificate. Brad will give a full report.

01-17-18	Permit 2017-68, 703 River Road. Hi Dave, this email is to inform you that 	Final Building Department and Life Safety inspection has been completed

for the Clinical Center building at 703 River Road, Plainfield NH. Your

Inspector as well as the Fire Chief and myself were together and reviewed

all aspects of work preformed and found all conditions acceptable with

these four exceptions.

fire extinguishers needed to be placed, one on ea. floor.

add touch up fire stopping at mechanical room.

improve the R rating at the attic access hatch

seal void in ceiling at GDR in office.

I was told it would be acceptable to submit photos of these items once the

work is complete. The following pictures are documenting those items have 		been addressed. I believe the only outstanding condition remaining to be

met is that a stamped engineered design for the fire alarm must be

submitted for town records. Our project electrician is

working on getting that to you and you should see it soon.

01-22-18	Permit 2017-68, 703 River Road. Deane text me that the electrical service to the addition Carriage house is ready for inspection so Liberty Utilities can change over service from original service entrance to new one. Sent text to Brad as well as left phone message.

Time 0.1

01-23-18	Permit 2017-68, 703 River Road. Text from Deane that he emailed me stamped drawings. Downloaded and sent to Town Office,  and Brad. Also notified Liberty Utilities it was okay to change over service.

Time 0.5

02-02-18	Permit 2017-68, 703 River Road. I met with Dean (Pilot), A VLS Rep, and a Mountain Valley rep this morning for the final inspection of the Carriage House, We walked through all of the rooms of the building. On the construction/renovation activities everything looked complete with the exception of minor painting in progress. All finishes, fixtures, and fittings were in place and areas were free of construction/renovation debris.

I checked Fire alarm fixtures in each room against those called for on the drawings. Everything appeared to be as called out.

We proceeded to the Mechanical Room where I observed a test of the alarm system as triggered by a simulated activation of the sprinkler system. I saw the flow triggered, the pump activate, and heard the alarms activate in the carriage house and (via radio) the main building (the old Inn). Dean and the VLS Rep explained how they had previously conducted a “Bucket test” by activating a sprinkler head near the end of the line in the occupied space and discharging into a couple of 30 gal containers. They verified that the system maintained pressure and flow as called for in the design.

I received 2 copies of the final stamped drawings, which I will drop of at the Town Hall.

I believe the project is complete. Let me know if you have any questions.

Regards,

Brad

02-02-18	Permit 2017-68, 703 River Road. I received Brads email and I issued a Certificate of Completion for the Carriage House and emailed to Deane.

Time 0.6

David H Lersch

Plainfield Building Inspector