Steve Beaupre’

PO Box 207

469-3004

Permit # 2014-55

Map/Lot 245/1

8 Red Hill Road

sfh with garage

08-07-14	Permit 2014-55, 8 Red Hill Road. Went by to inspect the footer forms. Part of the forms were there and due to the storm no one was on site.

Time 0.6

08-08-14	Permit 2014-55, 8 Red Hill Road. Footer forms constructed  but no ground wire and the rebar was setting on the ground around the outside of the forms. I called Tom and let him know that those items needed to be taken care of before I would give the okay to pour.

Time 0.5

08-10-14	Permit 2014-55, 8 Red Hill Road. I went by to see if the work was completed on the footer. Still the same.

Time 0.6

08-12-14	Permit 2014-55, 8 Red Hill Road. David, the concrete contractor called 08-11-14 and said he would be ready by morning and wanted the forms inspected. He said the rebar would be supported and tied together and asked for clarification on the ground wire. I went this morning and inspected the forms and they were ready for concrete. I gave David the go ahead and order concrete.

Time 0.7

08-19-14	Permit 2014-55, 8 Red Hill Road. Went by to see if the wall forms were ready. A few panels were up, but a long way from being ready.

Time 0.0

08-22-14	Permit 2014-55, 8 Red Hill Road. Inspected the wall forms and they had two rows of rebar and looked okay.

Time 0.4

09-11-14	Permit 2014-55, 8 Red Hill Road. I inspected the perimeter drains both outside the foundation wall as well as inside. Two inches of blue foam installed on the outside of the foundation up to the plate. They still need one inch and it will go on the inside of the foundation. There is a window in the basement wall for egress and I let them know the requirements. Okay to backfill.

Time 0.3

10-01-14	Permit 2014-55, 8 Red Hill Road. Inspected the foundation wall forms for the attached garage. Okay to pour.

Time 0.5

10-15-14	Permit 2014-55, 8 Red Hill Road. Tom called and asked me to inspect the drain plumbing that will be under the garage section's slab so they could install blue foam, then pour the floor.

Time 0.1

03-29-15	Permit 2014-55, 8 Red Hill Road. Went by to see the progress that has occurred since I have been away. It was framed and had sheathing on the outside and panels on roof.

Time 0.2

04/30/15	Permit 2014-55, 8 Red Hill Road. Went to meet Tom to go over dryer vent 		codes and to do a rough in electrical inspection. Tom wasn't there yet so I 			did the rough in electrical inspection and it looked okay except I had a few 		questions. Went to Town Hall to drop off CO for Ledge Lane and call 			Tom.

Time 0.5

Called Tom and he said he would meet me at the house. The code for 			dryer vents is a maximum of 25' with elbows using five feet. He wanted to 		go out the back of the house but the distance was way to far. There will be 			a front porch and if he has the vent come out under the porch it would 			meet code. We also went over the electrical in the kitchen to meet the four 			foot rule on kitchen counters. He was going to insulate. I told the 				electrician that he needed to fire stop holes in the plates.

Time 0.8

05-14-15	Permit 2014-55, 8 Red Hill Road. I got there to inspect the rough in plumbing. They still needed to fire stop the holes and pressure test the sewer pipes and water lines. Tom said that the plumber is coming this weekend to finish and for me to come by Monday to inspect as they wanted to start to hang sheetrock.

Time 0.6

05-18-15	Permit 2014-55, 8 Red Hill Road. I inspected the fire stopping and a few places needed to be filled, new holes. The sheetrock installers filled the holes. The pressure on the water lines and the sewer lines were zero. called Tom and he was going to get the plumber back to pressurize the lines again. Tom will make sure it is fixed and let me know what was the problem. The sheetrock installers would not cover any walls with plumbing until it is fixed.

Time 0.6

06-08-15	Permit 2014-55, 8 Red Hill Road. Met with Tom and electrician to inspect the trench for the buried electric from the pole to the pedestal to the house.

Looked okay. They will call when the wires are run and the trench is filled.

Time 0.5

06-11-15	Permit 2014-55, 8 Red Hill Road. Inspected the electrical service entrance and looked okay. I notified Liberty Utilities after I got home as I needed to go online to check my email to find the telephone number. I left a message with my old ID and password from National Grid to say that work order #8830-18000696 is ready to be connected.

Time 0.9

08-07-15	Permit 2014-55, 8 Red Hill Road. Met with Tom to do the final inspection of the single family home. The height of the smoke/co detector in the living/bedroom (was going to be the garage) needed to be closer to the ceiling and in the hallway outside that room was missing a smoke/co detector. I told Tom I would process the Certificate of Occupancy, but would verify that the work was completed.

Time 1.5

08-20-15	Permit 2014-55, 8 Red Hill Road. Went by and the detector issue wasn't fixed yet.

Time 0.4

09-22-15	Permit 2014-55, 8 Red Hill Road. Detectors installed.

David H Lersch

Plainfield Building Inspector