Ira & Sara Townsend

83 Columbus Jordan Road

469-3313

Permit #2009-01

Map/Lot 234/4

Upgrade 60amp. service to 100amp. service

01-28-09	Permit 2009-01, 83 Columbus Jordan Road. Met with electrician, NH Co-Op rescheduled for the next day, to inspect the new 100amp. panel and new meter socket. There is a transfer switch between the meter and the new panel. The meter is on the front corner of the house and will be moved to the end when the attached building is removed. He ran into a lot of ledge and could not drive the ground rods in more than half way even with a jack hammer. Due to the volume of snow, I told him he could drive one as far as possible and connect the new ground wire to it and temporary connect to the existing ground wire. I will keep the permit open as when they move the meter in the spring they will finish installing the new ground wire. I will email NH Co-Op of this as well.

Time 0.9

07-28-11	Called Peabody Electric and left message about ground rods.

David H Lersch

Plainfield Building Inspector