MVWD

PO Box 84, Meriden

Permit # 2017-83

Map/Lot #105/14

53kw GROUND MOUNTED SOLAR

90 Bonner Road

04-23-18	Permit 2017-83, 90 Bonner Road. I inspected the trench from the utility pole to the back fence with conduit and tape installed. Also the partial construction of the large pedestal that will have the building disconnect, the solar disconnect and meter. I will have to go back and inspect when they change power for the building to the new panel with Liberty there.

Time 0.3

04-30-18	Permit 2017-83, 90 Bonner Road. Met with contractor and Liberty to inspect the new electrical panels, cables, and the work to change building service to new service entrance. Notified Liberty via email and Liberty servicemen that is okay to reconnect.

Time 0.3

06-18-18	Permit 2017-83, 90 Bonner Road. I met with Norwich solar and completed the final inspection of the solar installation. I signed the form for the power company and I will issue a Certificate of Completion.

Time 0.8

David H Lersch

Plainfield Building Inspector