Kimball Union Academy

PO Box 188

Meriden

469-2166

Permit # 2011-33

Permit 2012-48

103/4

Metal Building for Soccer Field

20 Campus Center Way

03-21-11	KUA. I met with Doug Plummer and others to go over the preliminary plans for the soccer field building. It will not be regulation size and will be used for team practice. They are not planning installing any bleachers, as the entire inside area of the building will be the field. They are looking at a maximum capacity of 300 for code issues. There will be a double set of doors at each end of the building. They want to add a fitness center with bathroom facilities to the end of the building when the funds become available so it seems pointless to add a small facilities building and in two years tear it down to build the fitness center. The ice rink building is close by and would be left open when needed to provide temporary bathroom facilities. When the building is completed, I told them a CO would be issued contingent on the completion of the fitness center within two years.

Time 0.9

04-26-11	KUA, I met with Doug and others to review the snow load calculations the

contractors bidding on the project submitted. The calculations were okay

and a copy will be on file at the town office.

Time 0.3

06-03-11	Permit none, KUA Field House. Met with the contractor KUA selected

and KUA personnel to go over the project.

Time 0.9

08-22-11	Permit 2011-33, 20 Campus Center Way. I received a call from Jim to inspect the forms they were going to pour. Jim and I walked around the perimeter and discussed what was going to be done. They had poured a large bed of concrete in the trench without using forms so they had a good base to build the pier forms on and on the right side where they need to build retaining walls to bring that side up to level so they can build the pier forms. It matched the plans I have. I will be going back each day as they will be forming and pouring each day.

Time 0.7

08-23-11	Permit 2011-33, 20 Campus Center Way. Everything was too wet and they were trying to pump out the water so they could install the rebar and pour. On the lower, right side they had poured some of the retaining walls and were backfilling. Jim and I discussed how they were going to build the low side in a step configuration (like a pyramid), backfilling as they go.

Time 0.9

08-24-11	Permit 2011-33, 20 Campus Center Way. I inspected the pier forms that had the rebar installed and were poured. They still are having issues with the water from rain and seepage from under the tennis courts. I also inspected the footer forms for the front wall. Looked okay.

Time 0.4

08-25-11	Permit 2011-33, 20 Campus Center Way. I inspected the pier forms on the right side that were almost ready for pouring. The left side adjacent to the tennis courts still had water in the forms. Due to the rain predicted for tonight, they wouldn’t come in tomorrow, but would be back next week.

Time 0.5

08-31-11	Permit 2011-33, 20 Campus Way. I stopped by to see how things were going. More of the forms were built on the lower side to continue to build up to the level for the pier forms. Several pier forms on the right near the front end were poured.

Time 0.3

09-01-11	Permit 2011-33, 20 Campus Way. Stopped by to see the progress of the forms and the concrete pours. It looks like all the pier forms on the right are poured and the future retaining walls between the piers still have a lot of site from the rain.

Time 0.4

09-08-11	Permit 2011-33, 20 Campus Way. Stopped by to see how things were progressing. Saw Jim and they were pouring the pier forms on the left side. All the rebar was installed and the bolts for anchoring the metal supports.

Time 0.2

09-30-11	Permit 2011-33, 20 Campus Center Way. Stopped by to see the progress. Almost all the concrete work for the walls was completed except for two sections between the piers on the right side near the rear. They were having trouble with all the rain and these last sections they are going to use concrete blocks with rebar installed every three rows. They are setting the upright steel on the piers and next week they should start building the trusses on the ground and then mounting them on the uprights.

Time 0.4

10-04-11	Permit 2011-33, 20 Campus Center Way. I went by to see the progress they were making. All the upright steel was installed and anchored to concrete piers.

Time 0.2

10-13-11	Permit 2011-33, 20 Campus Center Way. I saw one of the roof trusses installed yesterday when I was driving by and went today to inspect the site. They had taken down the roof truss. The wall sections between the piers were done with concrete blocks with vertical rebar and well as horizontal rebar every three rows. They still have three more sections to do. They were building the retaining wall for the bank along the tennis courts using the same procedure that they are using for the wall between the piers. Everything looked okay. I told them to let Jim know I will stop by next Friday.

Time 0.5

10-20-11	Permit 2011-33, 20 Campus Center Way. They were still working on laying concrete block for the wall next to the tennis court. I looked at the pier that was cracked when the truss was being mounted on the uprights and according to the contractor when the truss was being lined up on the other end it was raised to high putting stress on the pier where normally there wouldn’t be stress in that direction. I told the I wanted the structural engineer’s report on the plan of action for the cracked pier.

Time 0.7

10-25-11	Permit 2011-33, 20 Campus Center Way. I met with Jim and went over the project. They are almost completed with the retaining wall by the tennis court and once several of the roof trusses are installed, they will work on the last three sections of the retaining walls on the right side. They had two trusses installed and were installing the steel between the two trusses. We discussed the cracked pier as well. (Note: Steve told me that the reports from the contractor’s engineer would be given to KUA’s engineer to review and I let Steve know I already asked for a copy from Jim.) I am not sure how to address the sections of the retaining walls that are deformed due the forms giving way because of all the rain and mud. It appears they are structurally sound and if KUA is unhappy with the wall shapes, they can address it with the contractor.

Time 0.4

10-31-11	Permit 2011-33, 20 campus Center Way. After seeing Steve at the town hall I stopped by to see the progress. The main part of block wall along the tennis court was built, but still needs a cap on top of the wall and a right angle section from the bank along the front to match the grade there. No additional trusses installed.

Time 0.3

11-10-11	Permit 2011-33, 20 Campus Center Way. I stopped by to see how things were progressing. They had all but three trusses installed. A new crane company was there and using two cranes. The steel workers said that they should have the last of the trusses installed tomorrow and said this company was doing a better job. There is only one section on the right rear corner that is not completed as far as the retaining walls.

Time 0.5

11-18-11	Permit 2011-33, 20 Campus Center Way. I received a call from The State Fire Marshall, Ken Walsh, to meet with him at KUA regarding issues with the building. I met with Frank, Fire Chief; Ken; Steve Rook with OSHA and the contractor Jim at the site. There was a complaint from a contractor that was fired that the structure wasn’t safe. There were several issues, one is that OSHA felt that some of the workers weren’t qualified to be working on the steel structure. The other main issue is that the retaining walls should have been poured according to the PE and Jim started using concrete blocks without a PE approval, also the construction of the piers were poured in layers and should have been one pour per pier. We had a conference call with the PE who designed the concrete work and found out he wasn’t certified in NH. A can of worms. The contractor had two choices-one to have a crew add all the bracing and aligning the steel structure to make it safe or take it all down. The concrete work has to be inspected and signed off by a PE stating that it is okay to continue building the structure or if he won’t sign off it all has to be completely torn down.

Ken called me later after I got home and suggested to let the State Fire Marshall’s Office take over the administration of the permit. I told him I thought it would be okay with me and Frank agreed. I will draft a letter to Ken and discuss with Steve on Monday as I will meet at KUA sometime on Monday with Ken.

Time 4.0

11-21-11	Permit 2011-33, 20 Campus Center Way. Met with Steve (OSHA), Ken (Dept. of Safety) and Steve at the town hall to go over the KUA project. Steve and I gave a letter to Ken, asking for their assistance in the administration of the KUA building.

Time 1.3

11-24-11	Permit 2011-33, 20 Campus Center Way. Read over construction manual for the erection of the steel building.

Time 0.3

11-29-11	Permit 2011-33, 20 Campus Center Way. Department of Safety called meeting at KUA with contractor, engineers, OSHA, KUA, Fire Chief, and Town Officials. Reviewed pictures and developed an action plan that should have possible solutions in three weeks.

Time 3.4

NOTE: 	Original contractor was let go and the entire concrete work was removed and the steel was torn down and stored on site.

08-15-12	Permit 2012-48, 20 Campus Center Way. I met with the contractor, the structural engineer, Doug Plummer, Ron from the fire marshal office. We inspected the forms along the tennis court and on the rear of the building. It will be one continues pour with about 100 yards of concrete. Ron will inspect any new forms along with me or he will have a consultant inspect the forms.

Time 1.7

08-21-12	Permit 2012-48, 20 Campus Center Way. Dan the contractor called me to say that they had the forms for the lower side ready for inspection and wall forms in place for part of the tennis court side and pert of the rear. The forms for the piers and the wall were made so the concrete would be one piece.

Time 0.7

08-28-12	Permit 2012-48, 20 Campus Center Way. I inspected the wall forms along the tennis court that had all the rebar installed and inspected on a prior inspection. The wall section that was poured looked okay. I inspected the footer forms and rebar on the lower side, center section, and they were hoping to get the next section ready with rebar to pour later today. The rear section of the lower side that was poured on the 21st has all the vertical rebar installed and is ready for the wall forms. All was okay.

Time 0.8

08-28-12	Permit 2012-48, 20 Campus Center Way. I inspected the next section of footer forms on the lower side up to where the there is a step up. Looked okay.

Time 0.3

08-29-12	Permit 2012-48, 20 Campus Center Way. Dan emailed me to inspect the last section of the tennis court wall rebar so they could put up the wall forms. Looked okay, same as the rest of the wall. Ron will be by Thursday to inspect as well as they want to pour next week.

Time 0.7

09-04-12	Permit 2012-48, 20 Campus Center Way. I inspected the last section of footer on the lower side. It is a step up from the rest and looked okay except the additional horizontal rebar that goes side to side wasn’t there. I will check on it. It was pouring, so there wasn’t anybody working yet.

Time 0.4

09-06-12	Permit 2012-48, 20 Campus Center Way. I inspected the rebar for the wall forms on the lower side as they were installing wall forms on the section that was previously inspected and wanted to install the forms up to the step in the footer. I inspected the rebar that was completed while I was there and I would have to come back to view the rest when they were done. It would be ready by the end of the day and wanted to pour tomorrow. I said I would come by at seven tomorrow and inspect. Also a not to the comment about the horizontal rebar on that last section of footer. Dan said that that last section didn’t need the extra rebar per design.

Time 0.5

09-07-12	Permit 2012-48, 20 Campus Center Way. I inspected the wall forms and the rebar that was installed. It was the same as the rest of the walls.

I told Dan it was okay.

Time 0.6

09-11-12	Permit 2012-48, 20 Campus Center Way. I went to inspect the footer forms for the front end of the building. All the forms were there, but only some of the rebar was installed from the right corner to about one third of the forms. They were going to pour the next day and someone from the state was supposed to come by later or in the morning to inspect the forms.

Time 0.7

09-12-12	Permit 2012-48, 20 Campus Center Way. I stopped around eleven o’clock to see if the forms were ready. They were pouring concrete in the lower side wall forms and all the rebar was installed in the front end wall footer. Dan wanted to know what else needed inspected as he didn’t get the inspection sheet. I mentioned perimeter drains and they were installed and were being covered. The perimeter drains were installed on the inside of the rear end wall and the lower side wall and exits through the wall at the right rear corner. There are also perimeter drains installed on the outside of the left side wall and the rear end wall and connected to the other drains. They installed a drain on the outside of the lower side wall from the right rear corner towards the front for about one third of the wall (not required per design, but decided to do it because of all the water that usually collects on that rear corner). Just a note no one showed up from the state. The concrete testers were there taking samples and testing.

Time 1.0

09-14-12	Permit 2012-48, 20 Campus Center Way. The wall rebar was ready for inspection and I received an email to inspect so they could install the wall forms and pour concrete today. All the rebar was installed okay and some of the wall forms were already up for the front wall. This should be the last rebar/forms inspection except for the rebar that will be connected to the base of the piers. All the walls are now poured.

Time 0.6

09-21-12	Permit 2012-48, 20 Campus Center Way. Dan called to say that the last of the perimeter drains need inspected. The balance of the drains on the tennis court side and along the front end wall to the right corner then through the wall and along the inside of the right wall connecting to what was all ready inspected. Every thing looked okay. They were compacting the fill on the inside of the front wall and the tennis court side wall and the inspector was coming to test the soil.

Time 0.5

09-26-12	Permit 2012-48, 20 Campus Center Way. I received an email from Dan to inspect the rebar and concrete forms that will tie the piers together. They had two of the four ready for inspection. There were four runs of rebar that were screwed into the fittings previously installed to the rebar that was in the piers. Perpendicular to the rebar were rectangular shaped rebar spaced about four feet apart and the four lengths of rebar were tied to the four corners. Where the two runs, one from each pier, opposite each other met a coupling was installed. The other two that they want to pour should be ready by eleven tomorrow.

Time 0.4

09-27-12	Permit 2012-48, 20 Campus Center Way. I inspected the other two runs of rebar that were ready for concrete. Looked okay. They hope to have the next four ready for inspection about nine tomorrow.

Time 0.7

10-01-12	Permit 2012-48, 20 Campus Center Way. Delayed pouring due to rain. The last five runs of rebar and forms were ready today and were inspected. Everything looked okay. The next step will be to level and compact, then start erecting the steel.

Time 0.3

10-18-12	Permit 2012-48, 20 Campus Center Way. I met with Dan to go over the rest of the inspections as per his request. We discussed what would happen if I am out of town when it was complete. I told him by the time I may be gone most of the inspections will be completed except for the final and life safety. I told him I would have the Fire Chief, Frank and the State Fire Marshals Office handle that and I would issue a CO and have it emailed and the original mailed to KUA. Most all the steel is up and they will be installing the insulation on the roof and the roof early November.

Time 0.6

11-15-12	Permit 2012-48, 20 Campus Center Way. I inspected the trench from the Ice Rink mechanical room to the right front corner of the field house. The conduit was installed and the water line was buried under the electrical conduit. Looked okay. All the siding was installed and they were getting ready to install the roof insulation.

Time 0.6

12-03-12	Permit 2012-48, 20 Campus Center Way. I met with Dan to inspect the electrical wiring. The panels were installed but did not contain anything yet. Wiring and ceiling lights were being installed as well as the ceiling insulation. I also looked at the propane forced hot air furnace that was being installed outside the rear of the building along with two large buried propane tanks.

Time 0.7

01-10-13	Permit 2012-48, 20 Campus Center Way. Time to read all emails from 1/21 until today and reviewing reports, etc. regarding requirements and the installation of fire safety equipment. There were issues about needing additional devices and also some needed to be relocated. All  emails that I sent or received were copied to a word document for reference.

Time 1.6

01-11-13	Permit 2012-48, 20 Campus Center Way. I received a call from Doug Plummer that the final inspection was completed. There were some issues when Ron, State Fire Marshall, was there yesterday and if they were taken care of we could issue an Occupancy Permit. Frank, Plainfield Fire Chief, did the inspection today and those items were taken care of and he issued a PERMIT TO OPERATE A PLACE OF ASSEMBLY. Doug emailed me the permit and I issued the Occupancy Permit and emailed it to Doug, Ron, Dan (GC), and asked Doug to forward to Frank as I didn't have his email. I will also email the Town Hall as well.

Time 0.9

David H Lersch

Plainfield Building Inspector