Kimball Union Academy

PO Box 188

Meriden

469-2152

Permit # 2017-10

Map/Lot 103/4

renovation of auditorium

60 Main Street

04-28-17	Permit 2017-10, KUA 60 Main Street. Inspected the rough in electrical 			wiring for the auditorium. Metal studs on block wall, nail plates over 			wiring in studs and low voltage for control of lights and USB charge ports.

They will be spraying foam insulation next week.

Time 0.8

05-04-17	Permit 2017-10 KUA 60 Main Street. Inspected the sprayed in foam 			insulation and the fire retardant paint above the drop ceiling.

Time 0.2

06-06-17	Permit 2017-10, KUA 60 Main Street. Inspected the wiring for the ceiling 			lights as they wanted to install the drop ceiling. Inspected the new   			electrical panel behind platform and some additional circuits for lighting 			and control circuits. Plans are for led lighting around the front exits fed by 			inverters that are motion sensor activated that will provide emergency 			lighting. Exit signs will be over the exit. Outside emergency lights were 			installed on rear entrance.

Time 0.6

08-04-17	Permit 2017-10, KUA 60 Main Street. While inspecting bathroom rough 			in for permit 2017-56, I completed the final inspection of the auditorium. I 		will issue a Certificate of Occupancy. All emergency lighting and exits 			installed.

Time 0.0

David H Lersch

Plainfield Building Inspector