Meriden Village Development

Traditional 359-3161

Permit #4061 Lot 11 (11 Baynes CO issued)

Permit #4075, 6072 Lot 1 (shell built 8 Baynes)

Permit #4082, 7009 Lot 3 (10 Baynes)

Permit #5005 Lot 10 (13 Baynes)

Permit #5020 Lot 5 (16 Baynes)

11-22-04	Permit 4061, 4075, Meriden Village Development. Met with project manager, Argus; foundation, Dave Kelly; and the electrician. Inspected foundation with 4” drain pipes that will be under the basement floor for radon venting on what is lot 1, 2nd site had the footer poured and ready for the walls. Lot 11 is all framed and the electrician was just getting started. Construction looked sound, 2x6 walls. Will do a more thorough inspection when the plumbing and electrical are roughed in. Footer poured for detached two car garage.

Time 01:00

11-30-04	Permit 4061, Lot 11 MVD. Inspected electrical wiring. Panel and service entrance not ready yet. Wiring to the detached garage coiled up outside waiting for construction of the garage and covered walkway from the house to the garage. Low voltage wiring for telephone, cable, and CAT5 cables were run in same holes as the 120VAC cables. The electrician was informed that was not according to code. Showed him the 800 section in the NEC pertaining to communication wiring. He will reroute the cables and I will inspect next time I am there. Also there was a lot of water along the front side of the house in the basement. The wall was wet a few inches above the floor. I will check next week when I inspect the plumbing and verify that the electrical items were fixed.

Time 0:50

12-03-04	Permit 4061, Lot 11 MVD. Angus called to set up inspection of the rough in plumbing for Monday morning.

Time 0:00

12-06-04	Permit 4061, Lot 11 MVD. Scheduled to inspect plumbing, plumbing not ready, inspected what was completed and verified that all low voltage wiring was rerouted per my prior visit. I will go tomorrow to finish the inspection of the plumbing.

Time 0:48

12-07-04	Permit 4061, Lot 11 MVD. The  waste plumbing was a capped off and pressure tested for the first and second floor. Plumbing still needs to be completed in the basement to connect to the sewer. The water in the basement was due to using a leaky garden hose in the basement. It appears to have dried up some.

Time 0:30

12-08-04	Permit 4082, Lot 3 MVD. Inspected perimeter drains, okay. Also mentioned to Angus that they needed to check on the permit for that site as it is not on the list.

Time 0:18

12-16-04	Permit 4075, Lot 1, MVD. Inspected the footer forms for the garage. Since they were not going to use reinforced concrete I told Angus Kelly that they should put in some rebar. There were vertical rods to attach the short foundation wall to the footer.

Time 0.3

12-23-04	Permit 5005, Lot 10. Inspected footer forms for the foundation of the house on Lot 10. Angus was informed that rebar and forms were okay and they could pour cement.

Time 0.5

01-11-05	Permit 5005, Lot 10, MVD. Inspected perimeter drain pipes installation and discussed material and procedure to cover pipes. All okay and told them to it was okay to backfill.

Time 0.5

04-22-05	Permit 5020, MVD Lot 5. Inspected footer forms prior to pouring concrete, okay.

Time 0:24

05-02-05	Permit 5020, MVD Lot 5. Inspected perimeter drains around footer and radon pipes. All was okay.

Time 0:20

06-10-05	Permit 5020, MVD lot 5. Inspected the footer forms for the attached garage. Told Angus it was okay to pour.

Time 0:25

06-16-05	Permit 5020, MVD Lot 5. Inspected garage wall forms. Ready to pour, gave okay.

Time 0:15

07-07-07	Permit 5020, MVD lot 5. Inspected rough in plumbing and electrical. Told Angus it was okay and I would call Granite State to let them know it was okay to hook up electrical service.

Time 0:30

09-12-05	Permit 5020, 16 Baynes Road, MVD Lot 5. I went and met with Keith to do a final inspection of this two story house. The new owner was there as well, Aurora Matzkin. The closing is on Thursday and they were still doing the radiant heat for the first floor and still had to connect all the runs to the manifold. The boiler was installed but not hooked up to propane yet. The rest of the plumbing was completed except for the supply lines in the first floor bathroom. The garage still needed two windows installed and they were working on the landscaping around the house. There is also a pair of steps that aren’t installed off the rear deck. I will need to go back tomorrow with Dave Best for the boiler inspection and a final before I issue the CO

Time 0:45

09-12-05	Permit 4061, MVD Lot 11. The house is completed and waiting for a buyer. I inspected the house and it is completed and looked okay. I told the project manager, Angus that I will document the fact the inspection was completed and when they have a buyer, I will issue the CO.

Time 0:15