DATE: 04/7/2020

Permit Status (Valid for one year from issue date)

Permit # 2019-01  		Issued:  02-10-2019

_X__	RENEWAL REQUIRED BY __02___/__10__/__2020___

____	NO INSPECTION REQUESTED

__X_ 	LAST INSPECTION:		02-16-2019

_X___ 	YOUR PERMIT REQUIRED INSPECTIONS PER  INSPECTION 				GUIDELINES.

____	CLOSED  – YOUR PERMIT IS CLOSED, A NEW PERMIT IS REQUIRED

____	A CERTIFICATE OF OCCUPANCY WAS REQUIRED PRIOR TO OCCUPYIING YOUR HOUSE

__X_	A CERTIFICATE OF COMPLETION WAS  REQUIRED

NAME: Walter Janes

ADDRESS : 1106 Route 12A

Plainfield, NH 03781

MAP: 	107  LOT 01			 ADDRESS:   Same

David H Lersch				     		603-381-1929

Plainfield Building Inspector

Walter Janes

1106 Route 12A

667-5040

Permit # 2019-01

Map/Lot 107/01

Upgrade to 200amp and panel in garage 100amp

01-16-19

From: Tsjellum van der Stok <tsjellum@gmail.com>
To: davejosie@juno.com
Subject: Electrical panel install in garage
Date: Wed, 16 Jan 2019 08:47:19 -0500
Hi David,
I am looking into installing an electrical sub panel in my garage, and am wondering if this is something that requires a permit and inspection. If so, can I do this work myself? I have a copy of NFPA-70, 2014.
I am also considering increasing the electrical service to my house from 100 A to 200 A. Do you know what portion of this work I can do myself?
Thank you,Walter JanesÂ

01-16-19

On Wed, Jan 16, 2019 at 10:13 AM David Lersch <davejosie@juno.com> wrote:
Any electrical work needs a permit, you will need to contact utility co. For work order to upgrade. Unless utility has an issue with you doing the service upgrade, you can do the work yourself. It will need to be inspected.

01-16-19

From: Tsjellum van der Stok <tsjellum@gmail.com>
To: David Lersch <davejosie@juno.com>
Subject: Re: Electrical panel install in garage
Date: Wed, 16 Jan 2019 14:46:49 -0500
OK, thank you. Who do I contact for a permit and to schedule an inspection?

01-16-19

On Wed, Jan 16, 2019, 3:51 PM David Lersch <davejosie@juno.com wrote:

Town hall has permit applications, call me to schedule inspections. With new circuit panel you will need to upgrade to new arc fault breakers per code. Town meets 1st and 3rd Wed. To approve permits. Check with utility to get a work order for 200amp upgrade. Service entrance req. Are online for each utility company.

01-17-19	1106 Route 12A, large Brick colonial across from the Grange.

I'm headed to fill out the permit tomorrow AM, and have the power company coming to take a look in the morning as well.

To clarify, when/if the permit is approved, I will schedule the power company to come and increase the service entrance size. I will then run 2/0 copper (or 4/0 aluminum) SER cable from the meter base to the new 200A panel. At what point do you need to inspect? I'm not sure of the order of operations here, any light you could shed would be much appreciated.

My answer same day. Inspection needed when he is ready to reconnect to utility, needs our approval before they will reconnect. Next inspection is when the panel is all wired.

1-25-19

Hi David,

To clarify, all the breakers in the panel must be arc fault, or just the 100A that feeds the garage. They are like 10x the price

01-28-19

My reply. The 100amp to garage is a standard breaker. The breakers in the garage need to be GFI unless there is living space in the garage. The new house panel will need to have correct breakers installed per NEC.

On Mon, Jan 28, 2019 at 3:11 PM David Lersch <davejosie@juno.com> wrote:

You may want to hire an elec. for advise on best and cost effective way to do what you want.

02-01-19

When do we schedule the inspection? Before the power company arrives, while they are there switching the wire over, or after the electric company has hooked up to the new meter socket?

02-01-19

On Fri, Feb 1, 2019 at 7:15 PM David Lersch <davejosie@juno.com> wrote:

I usually try to be there just before them, to inspect, then give them the okay to connect.

If it is the service for the house, they will disconnect power to old meter, you install new meter and have them scheduled to come back when you

think you will be ready and also schedule us.

02-01-19

OK, so Eversource will come and remove the service to the old meters (there are 2 meters feeding the house, one for the house, and one for the hot water heater. The power company has requested to remove them and replace with just one). I will connect the meter base to the 200A panel, at which point you will inspect. Then the power company comes and connects power from the road to the meter base.

I assume this all happens within a few hours, as the house will be without power (heat) during this time?

02-15-19

Hi David,

The house has a 20A double pole for the hot water heater, a 30A double pole for the dryer, and a 40A double

pole for the range. Do these need to be arc fault breakers? None of the businesses I have spoken with carry these, only the 15 and 20A single pole breakers.

Thanks,

Skip

02-15-19

On Fri, Feb 15, 2019, 3:19 PM David Lersch <davejosie@juno.com wrote:

No, refer to nec at town hall, only 120vac circuits

02-16-19

Hi David,

Have you spoken with Mr. Atwater? He mentioned that it may be possible to have the main service come into the 200A panel, and then feed the only 100A panel via a single 100A breaker.

REPLY - That can be done as long as Brad agrees.

Dave

05-19-20	Permit expired without final inspection.

David H Lersch

Plainfield Building Inspector