Hank Ruppertsberger

PO Box 106

675-2907

Permit #2018-71

Map/Lot 107/32

24x26 barn with ADU apartment

8 Daniels Road

10-02-18	Permit 2018-71, 8 Daniels Road. Met with Pete to go over project. Covered inspections of trench for electric, slab requirements including ground wire.

Time 0.5

10-17-18	Permit 2018-71, 8 Daniels Road. Inspected the trench and perimeter drains from the house to the road then to the field on the right side of the house.

Trench for power not ready.

Time 0.2

10-17-187	Permit 2018-71, 8 Daniels Road. Inspected the trench for the water, sewage and electric. Looked okay.

Time 0.3

10-25-18	Permit 2018-71, 8 Daniels Road. Met Pete and inspected the pad for the generator and conduit in the trench to the garage. Inspected the forms for the garage floor and the short knee wall that will be poured in one step. Blue foam insulation under garage floor and around perimeter extending out from the wall. Several rows of rebar installed and wire mesh. Ground wire clamped to rebar. Also saw propane tank and trench for line to the house with the tank in the ground but not buried yet.

Time 0.3

04-25-19	Permit 2018-71, 8 Daniels Road. Inspected the framing for the two story garage. Windows were being installed and the wood siding. The generator will not be installed at this time as well as the upstairs will not be finished into an apartment. Looked okay.

Time 0.3

12-31-19	Called Hank before Christmas and recommended he renew permit if he wants to eventually finish apartment. If not I will have Brad do a final when ready.

11-17-20	Met with Hank to go over plans to finish apartment. He will build a wall to create an entrance way from side entrance door to stairs, will be insulated and 5/8ths fire code sheetrock. The ceiling will be insulated to R30 and have sheetrock installed. The entrance way all walls will be insulated and have sheetrock installed. Under the stairs will house the utility room and will be insulated and will have sheetrock installed on walls and under stairs. The upstairs will be open with some partial walls. Walls will have R20, sloped ceiling will have R38 and flat ceiling will have R49, problably blown in insulation. There will be two doors on the new wall downstairs, one to enter the entry and one to enter the mechanical room, both will be 1/2 hour fire rated. He will be using a heat pump and some other heat source for the bitter cold weather. All plans looked okay and he made notes of requirements we discussed. I let him know he should renew his permit and he said he was planning on it and would get it renewed. I forgot to send him a reminder letter as I have been doing.

Time 0.8

06-02-21	Inspected the new service entrance panel with meter socket and disconnect

on left side of garage. Main entrance cable went to generator transfer switch that feed 200 ampere circuit panel. Notified Eversource it was okay to change service from house to garage.

Time 0.4

07-15-21	I inspected the rough in electrical and plumbing for the ADU, looked okay. Some areas need metal plates, will talk to Hank. I can also check

both the plates and fire stopping on next inspection.

Time 0.3

01-08-22	Hank sent me pictures of all the insulation for his garage with the upstairs ADU and I approved the installation of the sheetrock. Sent text to Hank that permit wasn't renewed.

Time 0.2

01-13-22	Hank said he renewed last November, told me to check with Michelle.

Checked with Michelle and my records and could not find anything except

the letter I sent to have him renew. He said he paid for permit and two renewals. Text him 10-2018 to 2019, 10-2019 to 2020, 10-2020 to 2021,

needs 10-2021 to 10-2022. Said he would renew.

Time 0.4

01-18-22	Hank called about door to stairs and mechanical room as to fire rating.

Time 0.2

David H Lersch

Plainfield Building Inspector

January 24, 2020

Henry Ruppertsberger

PO Box 106

8 Daniels Road

Plainfield, NH 03781

Your current building permit 2018-71 with a expiration date of 10-03-19 has been renewed and your new expiration date is 10-03-20 for a 24'x26' garage/ADU at 8 Daniels Road, Map 107 Lot 32. Original permit number was 2018-71.

All work must conform to the current building codes, (go to plainfieldnh.org, Documents/Building Inspection/NH Adopted Codes).

Please refer to the Inspection Guidelines document at plainfieldnh.org, Documents/Forms/Building Inspection Guidelines).

If you need to contact me, email me at inspector@plainfieldnh.org

_____________________________________

David H Lersch

Plainfield Building Inspector              603-381-1929

December 8, 2020

Hank Ruppertsberger

PO Box 106

Plainfield, NH 03781

Your current building permit 2018-71 with a expiration date of 10-03-2020 has been renewed and your new expiration date is 10-03-2021 for renovating building to barn with a second floor accessory dwelling unit 8 Daniels Road, Map 107 Lot 32.

All work must conform to the current building codes, (go to plainfieldnh.org, Documents/Building Inspection/NH Adopted Codes).

Please refer to the Inspection Guidelines document at plainfieldnh.org, Documents/Forms/Building Inspection Guidelines).

If you need to contact me, email me at inspector@plainfieldnh.org

_____________________________________

David H Lersch

Plainfield Building Inspector

603-381-1929